## Invul Blad
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
Condensation with aquatherm blue pipe SDR7,4/11/17,6 MF vs Seamless Carbon Steel and Copper pipe
Only the green cells can be edited
Condensation:
In the air there is always an amount of water vapour. By cooling off this air on a cold pipe, condensation will occur
on the outside of the pipe. This condensation is caused by the combination of the outside wall temperature of the
pipe and the relative humidity (RH).
Relative humidity (RH):
The ratio of the actual amount of water vapour in the air to the amount it could hold when saturated, expressed as a percentage OR
the ratio of the actual vapour pressure to the saturation vapour pressure, expressed as a percentage.
The amount of water vapour the air can hold increases with temperature. Relative humidity therefore decreases with increasing temperature
if the actual amount of water vapour stays the same.
|  | λ [W/mK] aquatherm blue pipe | λ [W/mK] Steel | λ [W/mK] Copper | α Water (W/m²K) | α Air (Default) (W/m²K) |  |  | λ = Thermal conductivity [W/mK]
|  | 0.15 | 50 | 384 | 1000 | 15 |  |  | α = Heat transfer coefficient [W/m²K]
The following data are theoretically determined.
For example: for the exact air flow into the area, we can not record real terms, since we do not know the site conditions.
For the below calculations (row 39) we use an avarage α Air value of 15 W/m²K (slight airflow around pipe)
If you want to use another value, you can change this in cell D42.
Since the λ value of the aquatherm blue pipe is lower than the λ value of steel or copper pipes, aquatherm blue pipes will condense less quickly.
[10 empty] | ⁰C | ⁰F | K
For the dimension of the aquatherm blue pipe you can only chose from the existing sizes: | [9 empty] | 18.04 | 64.472 | 291.2
20* / 25* / 32** /40** / 50** / 63** / 75** / 90** / 110** / 125** /160** / 200** / 250** / 315** / 355** / 400*** / 450*** / 500*** / 560*** and 630***mm. | [9 empty] | 5.5556 | 42 | 278.7156
( * = SDR7,4 ** = SDR11 *** = SDR17,6 ) | [9 empty] | -0.16 | 31.712 | 273
aquatherm blue pipe MF external pipe dimension [mm] | DN | aquatherm blue pipe MF | Seamless Carbon Steel pipe | Copper pipe | Chilled water temperature | Ambient temperature | Condensation on aquatherm blue pipe MF at relative humidity of: | Condensation on Seamless Carbon Steel pipe at relative humidity of: | Condensation on Copper pipe at relative humidity of: | aquatherm blue pipe MF outside wall temperature (°C) | Seamless Carbon Steel outside wall temperature (⁰C) | Copper outside wall temperature (⁰C)
|  | SDR7,4/11/17,6 | DIN 2448 | AS1432:2000 type B | °C | °C
32 | 25 | 32 x 2,9 | 33,7 x 2,6 | 31,8 x 1,2 | 1 | 30 | 27.73% | 17.68% | 17.68% | 8.34 | 1.53 | 1.47
α Air | W/m²K | W/m²K | The adjacent data are based on the |  |  |  | Condensation on aquatherm blue pipe MF at relative humidity of: | Condensation on Seamless Carbon Steel pipe at relative humidity of: | Condensation on Copper pipe at relative humidity of: | aquatherm blue pipe MF outside wall temperature (°C) | Seamless Carbon Steel outside wall temperature (⁰C) | Copper outside wall temperature (⁰C)
still air | 8 | 8 | selected α Air value (cell D42) and the
fast moving air | 30 |  | above selected diameter and temperatures |  |  |  | 22.95% | 17.43% | 17.31% | 5.44 | 1.29 | 1.25
If according to the above calculations the pipe will still condense, you should insulate the pipe.
In the below green cells (B50 and C50), you can select the λ value of the insulation and the insulation thickness.
The Relative Humidity (RH) in the below cells (I50, J50 and K50) are calculated with the α Air selected in cell D42
λ Insulation (W/mK) | Insulation thickness [mm] | The adjacent data are based on the selected α Air value (cell D42), selected insulation (B50) and insulation thickness (C50) |  |  |  |  | Condensation on (aquatherm blue) pipe insulation at relative humidity of: | Condensation on (Steel) pipe insulation at relative humidity of: | Condensation on (Copper) pipe insulation at relative humidity of: | Insulation outside wall temperature (⁰C) | Insulation outside wall temperature (⁰C) | Insulation outside wall temperature (⁰C)
0.037 | 13 | and the above selected diameter and temperatures |  |  |  |  | 72.41% | 70.33% | 70.73% | 24.27 | 23.85 | 23.9
Armaflex | 0.037 W/mK |  |  | **** Please note!! Where the pipe is supported by metal pipe clamps or metal support beams, still air is formed.
Rockwool | 0.025 W/mK |  |  | Therefore you need to select an α Air value of 8 W/m²K.
To avoid the forming of condensation on the metal pipe clamps and/or support beams,
you need to select pipe clamps with a sufficient rubber lining.
The Lambda (λ) value of aquatherm PP-R of 0,15 W/mK was
tested by FIW. München ( Forschungsinstitut für Wärmeschutz e.V München )
signed by Dipl.-Ing. H.Zehendner and Dipl.-Ing. (FH) W.Albrecht.
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on B39: Chose pipe dimension: 20 / 25 / 32/ 40 / 50 / 63 / 75 / 90 / 110 / 125 / 160 / 200 / 250 / 315 / 355 / 400 / 450 / 500 / 560 / 630
Note on I39: Relative humidity calculated with * α Air = 15 W/m²K * λ aquatherm PP-R * No insulation
Note on J39: Relative humidity calculated with * α Air = 15 W/m²K * λ Steel * No insulation
Note on K39: Relative humidity calculated with * α Air = 15 W/m²K * λ Copper * No insulation
Note on D42: Variable α Air value to be selected. Min 8 W/m²K, max. 30 W/m²K
Note on I43: Relative humidity calculated with * α Air selected in cell D42 * λ aquatherm PP-R * No insulation
Note on J43: Relative humidity calculated with * α Air selected in cell D42 * λ Steel * No insulation
Note on K43: Relative humidity calculated with * α Air selected in cell D42 * λ Copper * No insulation
Note on I50: Relative humidity calculated with * α value selected in cell D42 * λ aquatherm PP-R * λ Insulation cell B50 * Insulation thickness cell C50
Note on J50: Relative humidity calculated with * α value selected in cell D42 * λ Steel * λ Insulation cell B50 * Insulation thickness cell C50
Note on K50: Relative humidity calculated with * α value selected in cell D42 * λ Copper * λ Insulation cell B50 * Insulation thickness cell C50

## cond ber
Alpha luchtl | W / m2°C
stilstaande lucht | 8
bewegende lucht | 30
Pas op! in de onderstaande gegevens is gerekend met 2 verschillende alpha's nl. 8 en 15
Waarde 8 alleen toepassen bij beugel en halfschaal omklemming. ( voor berekening condensatie beugel of halfschaal )
Waarde 15 aangenomen als gemiddelde voor bewegende lucht
Pas op! Deze waarde kunt u ook zelf aanpassen indien u meer of minder circulatie van lucht verwacht.
PAS op alleen de groene vakken aanpassen. | [8 empty] | #DIV/0!
| voor buis maten zie onderstaande laatste tabel | [5 empty] | 0.02451 | 1.3333 | 0.6778
Climatherm Fusiotherm
Diameter (mm) | Wanddikte (mm) | Binnen- diameter (mm) | Delta T (°C) | Alfa water (W/m2x°C) | Alfa lucht (W/m2x°C) | Lambda (W/mx°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J) | Q=AxkxDelta T (W/mtr) | T omgeving (°C) | Delta T = Q/(1/(Alfa2xd2)) | aquatherm blue pipe MF outside wall temperature (°C)
32 | 2.9 | 26.2 | 29 | 1000 | 8 | 0.15 | 0.038168 | 3.9062 | 0.66659 | 0.68132 | 19.7584 | 30 | 24.5675 | 5.4325 | 10.8301 | 5.44
32 | 2.9 | 26.2 | 29 | 1000 | 15 | 0.15 | 0.038168 | 2.0833 | 0.66659 | 1.1268 | 32.6769 | 30 | 21.6695 | 8.3305 |  | 8.34
(Voorbeeld: uitgaande van T omgeving is 20°C en T medium is 6°C)
Delta T | medium temp.
29 | 1
Staal volgens DIN 2448
Diameter (mm) | Wanddikte (mm) | Binnen- diameter (mm) | Delta T (°C) | Alfa water (W/m2x°C) | Alfa lucht (W/m2x°C) | Lambda (W/mx°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J) | Q=AxkxDelta T (W/mtr) | T omgeving (°C) | Delta T = Q/(1/(Alfa2xd2)) | buiswand temp (C°)
33.7 | 2.6 | 28.5 | 29 | 1000 | 8 | 50 | 0.035088 | 3.7092 | 0.0016759 | 0.83866 | 24.3211 | 30 | 28.7153 | 1.2847 |  | 1.29
33.7 | 2.6 | 28.5 | 29 | 1000 | 15 | 50 | 0.035088 | 1.9782 | 0.0016759 | 1.5591 | 45.2139 | 30 | 28.4708 | 1.5292 |  | 1.53
(Voorbeeld:Uitgaande van T omgeving is 20°C en T medium is 6°C)
33.7
Copper acc. AS1432 : 2000 Type B
Diameter (mm) | Wanddikte (mm) | Binnen- diameter (mm) | Delta T (°C) | Alfa water (W/m2x°C) | Alfa lucht (W/m2x°C) | Lambda (W/mx°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J) | Q=AxkxDelta T (W/mtr) | T omgeving (°C) | Delta T = Q/(1/(Alfa2xd2)) | buiswand temp (C°)
31.8 | 1.2 | 29.4 | 29 | 1000 | 8 | 384 | 0.034014 | 3.9308 | 0.00010218 | 0.79234 | 22.978 | 30 | 28.7504 | 1.2496 |  | 1.25
31.8 | 1.2 | 29.4 | 29 | 1000 | 15 | 384 | 0.034014 | 2.0964 | 0.00010218 | 1.4745 | 42.7617 | 30 | 28.5355 | 1.4645 |  | 1.47
(Voorbeeld:Uitgaande van T omgeving is 20°C en T medium is 6°C)
31.8
Climatherm Fusiotherm
PAS op dampspanning waarde C' zelf handmatig steeds aanpassen volgens tabel
Pas op alleen de groene vakken aanpassen.
omgeving temp. | Delta T (°C) | buis ABS |  | T buis wand (°C) | omgeving C' g/m3 | wand C' g/m3 | [5 empty] | condens bij rel vochtigheid |  | bij Alfa lucht (W/m2x°C)
30 | 29 | 32 | 2.9 | 5.4325 | 17.27 | 8.33 | [5 empty] | 48.23% |  | 8
30 | 29 | 32 | 2.9 | 8.3305 | 30.41 | 8.432 | [5 empty] | 27.73% |  | 15
Staal volgens DIN 2448
omgeving temp. | Delta T (°C) | buis STAAL |  | T buis wand (°C) | omgeving C' g/m3 | wand C' g/m3 | [5 empty] | condens bij rel vochtigheid |  | bij Alfa lucht (W/m2x°C)
30 | 29 | 33.7 | 2.6 | 1.2847 | 17.27 | 7.3 | [5 empty] | 42.27% |  | 8
30 | 29 | 33.7 | 2.6 | 1.5292 | 30.41 | 5.375 | [5 empty] | 17.68% |  | 15
Uitleg tabel: Omgevings temp. is 20°C met medium temp 6°C blijkt de buiswand temp. te zijn 8,1132°C
zie tabel onder bij temp 20 °C maximale hoeveelheid waterdamp bij relatieve vochtigheid 100% = 17,27 g/m3
zie tabel onder bij temp 8,1132 °C maximale hoeveelheid waterdamp bij relatieve vochtigheid 100% = 8,33 g/m3
condens treed op bij 8,33 :17,27 = 48,23% relatieve vochtigheid.
Dus als de wandtemp. van de buis hoger is dan 8,1132°C bij een relatieve vochtigheid van 48,3%, is er geen isolatie nodig.
Of als de relatieve vochtigheid minder is dan 48,3% bij een zelfde wandtemp. ( 8,1132°C ) , is er geen isolatie nodig
MAXIMALE DAMPSPANNING
Temperatuur °C | C' g/m3 |  |  | Temperatuur °C | C' g/m3
-10 | 2.17 |  |  | 10 | 9.4
-9 |  |  |  | 11 | 10
-8 | 2.53 |  |  | 12 | 10.66
-7 |  |  |  | 13 | 11.34
-6 | 2.98 |  |  | 14 | 12.06
-5 |  |  |  | 15 | 12.82
-4 | 3.51 |  |  | 16 | 13.63
-3 | 3.81 |  |  | 17 | 14.46
-2 | 4.13 |  |  | 18 | 15.36
-1 | 4.47 |  |  | 19 | 16.29
0 | 4.84 |  |  | 20 | 17.27
1 | 5.19 |  |  | 21 | 18.31
2 | 5.56 |  |  | 22 | 19.4
3 | 5.88 |  |  | 23 | 20.54
4 | 6.36 |  |  | 24 | 21.75
5 | 6.79 |  |  | 25 | 23.1
6 | 7.26 |  |  | 26 | 24.3
7 | 7.74 |  |  | 27 | 25.73
8 | 8.27 |  |  | 28 | 27.51
9 | 8.81 |  |  | 29 | 28.71
|  |  |  | 30 | 30.4

## diam
| DN | Climatherm | Steel | Copper | Climatherm | Steel | Steel | Copper | Copper
20 | 15 | 20 x 2,8 | 21,3 x 2,0 | 19,1 x 1.0 | 2.8 | 2 | 21.3 | 1 | 19.1
25 | 20 | 25 x 3,5 | 26,9 x 2,3 | 25,4 x 1,2 | 3.5 | 2.3 | 26.9 | 1.2 | 25.4
32 | 25 | 32 x 2,9 | 33,7 x 2,6 | 31,8 x 1,2 | 2.9 | 2.6 | 33.7 | 1.2 | 31.8
40 | 32 | 40 x 3,7 | 42,4 x 2,6 | 38,1 x 1,2 | 3.7 | 2.6 | 42.4 | 1.2 | 38.1
50 | 40 | 50 x 4,6 | 48,3 x 2,6 | 50,8 x 1,2 | 4.6 | 2.6 | 48.3 | 1.2 | 50.8
63 | 50 | 63 x 5,8 | 60,3 x 2,9 | 63,5 x 1,2 | 5.8 | 2.9 | 60.3 | 1.2 | 63.5
75 | 65 | 75 x 6,9 | 76,1 x 2,9 | 76,2 x 1,6 | 6.9 | 2.9 | 76.1 | 1.6 | 76.2
90 | 80 | 90 x 8,2 | 88,9 x 3,2 | 88,9 x 1,6 | 8.2 | 3.2 | 88.9 | 1.6 | 88.9
110 | 100 | 110 x 10,0 | 114,3 x 3,6 | 101,6 x 1,6 | 10 | 3.6 | 114.3 | 1.6 | 101.6
125 | 100 | 125 x 11,4 | 127,0 x 4,0 | 127,0 x 1,6 | 11.4 | 4 | 127 | 1.6 | 127
140
160 | 150 | 160 x 14,6 | 168,3 x 4,5 | 152,4 x 2,0 | 14.6 | 4.5 | 168.3 | 2 | 152.4
200 | 200 | 200 x 18,2 | 219,1 x 5,9 | 203,2 x 2,0 | 18.2 | 5.9 | 219.1 | 2 | 203.2
225 | 200 |  | 219,1 x 5,9 |  |  | 5.9 | 219.1
250 | 250 | 250 x 22,7 | 273,0 x 6,3 | N.A. | 22.7 | 6.3 | 273
315 | 300 | 315 x 28,6 | 323,9 x 7,1 | N.A. | 28.6 | 7.1 | 323.9
355 | 350 | 355 x 32,2 | 355,6 x 8,0 | N.A. | 32.2 | 8 | 355.6
400 | 400 | 400 x 22,7 | 406,4 x 8,8 | N.A. | 22.7 | 8.8 | 406.4
450 | 450 | 450 x 25,5 | 457,0 x 10,0 | N.A. | 25.5 | 10 | 457
500 | 500 | 500 x 28,4 | 508,0 x 11,0 | N.A. | 28.4 | 11 | 508
560 | 550 | 560 x 31,7 | 559,0 x 12,5 | N.A. | 31.7 | 12.5 | 559
630 | 600 | 630 x 35,7 | 610,0 x 12,5 | N.A. | 35.7 | 12.5 | 610
|  |  | Seamless Carbon Steel pipe |  | Copper pipe
|  |  | according DIN 2448 |  | acc. AS 1432 : 2000 type B

## Temp reeks
Temperatuur °C | C' g/m3
-10 | 2.17
-9
-8 | 2.53
-7
-6 | 2.98
-5
-4 | 3.51
-3 | 3.81
-2 | 4.13
-1 | 4.47
0 | 4.84
0.2 | 4.93
0.5 | 5.02
0.7 | 5.1
1 | 5.19
1.1 | 5.227
1.2 | 5.264
1.3 | 5.301
1.4 | 5.338
1.5 | 5.375
1.6 | 5.412
1.7 | 5.449
1.8 | 5.486
1.9 | 5.523
2 | 5.56
2.1 | 5.592
2.2 | 5.624
2.3 | 5.656
2.4 | 5.688
2.5 | 5.72
2.6 | 5.752
2.7 | 5.784
2.8 | 5.816
2.9 | 5.848
3 | 5.88
3.1 | 5.928
3.2 | 5.976
3.3 | 6.024
3.4 | 6.072
3.5 | 6.12
3.6 | 6.168
3.7 | 6.216
3.8 | 6.264
3.9 | 6.312
4 | 6.36
4.1 | 6.403
4.2 | 6.446
4.3 | 6.489
4.4 | 6.532
4.5 | 6.575
4.6 | 6.618
4.7 | 6.661
4.8 | 6.704
4.9 | 6.747
5 | 6.79
5.1 | 6.837
5.2 | 6.884
5.3 | 6.931
5.4 | 6.978
5.5 | 7.025
5.6 | 7.072
5.7 | 7.119
5.8 | 7.166
5.9 | 7.213
6 | 7.26
6.1 | 7.308
6.2 | 7.356
6.3 | 7.404
6.4 | 7.452
6.5 | 7.5
6.6 | 7.548
6.7 | 7.596
6.8 | 7.644
6.9 | 7.692
7 | 7.74
7.1 | 7.793
7.2 | 7.846
7.3 | 7.899
7.4 | 7.952
7.5 | 8.005
7.6 | 8.058
7.7 | 8.111
7.8 | 8.164
7.9 | 8.217
8 | 8.27
8.1 | 8.324
8.2 | 8.378
8.3 | 8.432
8.4 | 8.486
8.5 | 8.54
8.6 | 8.594
8.7 | 8.648
8.8 | 8.702
8.9 | 8.756
9 | 8.81
9.1 | 8.869
9.2 | 8.928
9.3 | 8.987
9.4 | 9.046
9.5 | 9.105
9.6 | 9.164
9.7 | 9.223
9.8 | 9.282
9.9 | 9.341
10 | 9.4
10.1 | 9.46
10.2 | 9.52
10.3 | 9.58
10.4 | 9.64
10.5 | 9.7
10.6 | 9.76
10.7 | 9.82
10.8 | 9.88
10.9 | 9.94
11 | 10
11.1 | 10.066
11.2 | 10.132
11.3 | 10.198
11.4 | 10.264
11.5 | 10.33
11.6 | 10.396
11.7 | 10.462
11.8 | 10.528
11.9 | 10.594
12 | 10.66
12.1 | 10.728
12.2 | 10.796
12.3 | 10.864
12.4 | 10.932
12.5 | 11
12.6 | 11.068
12.7 | 11.136
12.8 | 11.204
12.9 | 11.272
13 | 11.34
13.1 | 11.412
13.2 | 11.484
13.3 | 11.556
13.4 | 11.628
13.5 | 11.7
13.6 | 11.772
13.7 | 11.844
13.8 | 11.916
13.9 | 11.988
14 | 12.06
14.1 | 12.136
14.2 | 12.212
14.3 | 12.288
14.4 | 12.364
14.5 | 12.44
14.6 | 12.516
14.7 | 12.592
14.8 | 12.668
14.9 | 12.744
15 | 12.82
15.1 | 12.901
15.2 | 12.982
15.3 | 13.063
15.4 | 13.144
15.5 | 13.225
15.6 | 13.306
15.7 | 13.387
15.8 | 13.468
15.9 | 13.549
16 | 13.63
16.1 | 13.713
16.2 | 13.796
16.3 | 13.879
16.4 | 13.962
16.5 | 14.045
16.6 | 14.128
16.7 | 14.211
16.8 | 14.294
16.9 | 14.377
17 | 14.46
17.1 | 14.55
17.2 | 14.64
17.3 | 14.73
17.4 | 14.82
17.5 | 14.91
17.6 | 15
17.7 | 15.09
17.8 | 15.18
17.9 | 15.27
18 | 15.36
18.1 | 15.453
18.2 | 15.546
18.3 | 15.639
18.4 | 15.732
18.5 | 15.825
18.6 | 15.918
18.7 | 16.011
18.8 | 16.104
18.9 | 16.197
19 | 16.29
19.1 | 16.388
19.2 | 16.486
19.3 | 16.584
19.4 | 16.682
19.5 | 16.78
19.6 | 16.878
19.7 | 16.976
19.8 | 17.074
19.9 | 17.172
20 | 17.27
20.1 | 17.374
20.2 | 17.478
20.3 | 17.582
20.4 | 17.686
20.5 | 17.79
20.6 | 17.894
20.7 | 17.998
20.8 | 18.102
20.9 | 18.206
21 | 18.31
21.1 | 18.419
21.2 | 18.528
21.3 | 18.637
21.4 | 18.746
21.5 | 18.855
21.6 | 18.964
21.7 | 19.073
21.8 | 19.182
21.9 | 19.291
22 | 19.4
22.1 | 19.514
22.2 | 19.628
22.3 | 19.742
22.5 | 19.856
22.6 | 19.97
22.7 | 20.084
22.8 | 20.198
22.9 | 20.312
23 | 20.426
23.1 | 20.54
23.2 | 20.661
23.3 | 20.782
23.4 | 20.903
23.5 | 21.024
23.6 | 21.145
23.7 | 21.266
23.8 | 21.387
23.9 | 21.508
24 | 21.629
24.1 | 21.75
24.2 | 21.885
24.3 | 22.02
24.4 | 22.155
24.5 | 22.29
24.6 | 22.425
24.7 | 22.56
24.8 | 22.695
24.9 | 22.83
25 | 22.965
25.1 | 23.1
25.2 | 23.22
25.3 | 23.34
25.4 | 23.46
25.5 | 23.58
25.6 | 23.7
25.7 | 23.82
25.8 | 23.94
25.9 | 24.06
26 | 24.18
26.1 | 24.3
26.2 | 24.443
26.3 | 24.586
26.4 | 24.729
26.5 | 24.872
26.6 | 25.015
26.7 | 25.158
26.8 | 25.301
26.9 | 25.444
27 | 25.587
27.1 | 25.73
27.2 | 25.908
27.3 | 26.086
27.4 | 26.264
27.5 | 26.442
27.6 | 26.62
27.7 | 26.798
27.8 | 26.976
27.9 | 27.154
28 | 27.332
28.1 | 27.51
28.2 | 27.63
28.3 | 27.75
28.4 | 27.87
28.5 | 27.99
28.6 | 28.11
28.7 | 28.23
28.8 | 28.35
28.9 | 28.47
29 | 28.71
29.1 | 28.88
29.2 | 29.05
29.3 | 29.22
29.4 | 29.39
29.5 | 29.56
29.6 | 29.73
29.7 | 29.9
29.8 | 30.07
29.9 | 30.24
30 | 30.41
30.1 | 30.58
30.2 | 30.75
30.3 | 30.92
30.4 | 31.09
30.5 | 31.26
30.6 | 31.43
30.7 | 31.6
30.8 | 31.77
30.9 | 31.94
31 | 32.11
31.1 | 32.28
31.2 | 32.45
31.3 | 32.62
31.4 | 32.79
31.5 | 32.96
31.6 | 33.13
31.7 | 33.3
31.8 | 33.47
31.9 | 33.64
32 | 33.81
32.1 | 33.98
32.2 | 34.15
32.3 | 34.32
32.4 | 34.49
32.5 | 34.66
32.6 | 34.83
32.7 | 35
32.8 | 35.17
32.9 | 35.34
33 | 35.51
33.1 | 35.68
33.2 | 35.85
33.3 | 36.02
33.4 | 36.19
33.5 | 36.36
33.6 | 36.53
33.7 | 36.7
33.8 | 36.87
33.9 | 37.04
34 | 37.21
34.1 | 37.38
34.2 | 37.55
34.3 | 37.72
34.4 | 37.89
34.5 | 38.06
34.6 | 38.23
34.7 | 38.4
34.8 | 38.57
34.9 | 38.74
35 | 38.91
35.1 | 39.08
35.2 | 39.25
35.3 | 39.42
35.4 | 39.59
35.5 | 39.76
35.6 | 39.93
35.7 | 40.1
35.8 | 40.27
35.9 | 40.44
36 | 40.61
36.1 | 40.78
36.2 | 40.95
36.3 | 41.12
36.4 | 41.29
36.5 | 41.46
36.6 | 41.63
36.7 | 41.8
36.8 | 41.97
36.9 | 42.14
37 | 42.31
37.1 | 42.48
37.2 | 42.65
37.3 | 42.82
37.4 | 42.99
37.5 | 43.16
37.6 | 43.33
37.7 | 43.5
37.8 | 43.67
37.9 | 43.84
38 | 44.01
38.1 | 44.18
38.2 | 44.35
38.3 | 44.52
38.4 | 44.69
38.5 | 44.86
38.6 | 45.03
38.7 | 45.2
38.8 | 45.37
38.9 | 45.54
39 | 45.71
39.1 | 45.88
39.2 | 46.05
39.3 | 46.22
39.4 | 46.39
39.5 | 46.56
39.6 | 46.73
39.7 | 46.9
39.8 | 47.07
39.9 | 47.24
40 | 47.41
40.1 | 47.58
40.2 | 47.75
40.3 | 47.92
Climatherm buis temp | omgeving C' g/m3 | Climatherm wand C' g/m3 | Condensation on aquatherm blue pipe MF at relative humidity of:
5.4 | 30.41 | 6.978 | 22.95% | variable alpha waarde lucht
8.3 | 30.41 | 8.432 | 27.73% | vaste alpha waarde lucht 15
24.3 | 30.41 | 22.02 | 72.41%
staal buis temp | omgeving C' g/m3 | Staal wand C' g/m3 | Condensation on Seamless Carbon Steel pipe at relative humidity of:
1.3 | 30.41 | 5.301 | 17.43% | variable alpha waarde lucht
1.5 | 30.41 | 5.375 | 17.68% | vaste alpha waarde lucht 15
23.8 | 30.41 | 21.387 | 70.33%
staal buis temp | omgeving C' g/m3 | Copper wand C' g/m3 | Condensation on Copper pipe at relative humidity of:
1.2 | 30.41 | 5.264 | 17.31% | variable alpha waarde lucht
1.5 | 30.41 | 5.375 | 17.68% | vaste alpha waarde lucht 15
23.9 | 30.41 | 21.508 | 70.73%
omgevings temp
30
Condensatie van PP-R (80 ) Climatherm geisoleerd met Armaflex bij een rel vochtigheid van
onderstaande op variable Alpha waarde cel C28

## isoltie ber
|  |  |  | Climatherm FASER | [7 empty] | Lambda Armaflex
Diameter (mm) | Wanddikte (mm) | Binnendiam (mm) | Delta T (°C) | Alfa water (W/m2x°C) | Alfa lucht (W/m2x°C) | Lambda Faser (W/mx°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Armaflex (mm) | Lambda Armaflex (W/mx°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q=AxkxDelta T (W/mtr) | T omgeving (°C) | Delta T = Q/(1/(Alfa2xd2)) | T buiswand (°C)
32 | 2.9 | 26.2 | 29 | 1000 | 8 | 0.15 | 0.038168 | 2.1552 | 0.66659 | 13 | 0.037 | 8.0366 | 0.28831 | 8.361 | 30 | 5.7358 | 24.2642 | 24.27
33.7 | 2.6 | 28.5 | 29 | 1000 | 8 | 50 | 0.035088 | 2.0938 | 0.0016759 | 13 | 0.037 | 7.7275 | 0.31868 | 9.2418 | 30 | 6.1594 | 23.8406 | 23.85
31.8 | 1.2 | 29.4 | 29 | 1000 | 8 | 384 | 0.034014 | 2.1626 | 0.00010218 | 13 | 0.037 | 8.0746 | 0.30586 | 8.8699 | 30 | 6.1059 | 23.8941 | 23.9