## Capacity by velocity
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
Capacity of chiller units (secondary refrigeration systems)
in combination with
aquatherm blue pipe SDR7.4 /SDR11/SDR17.6 MF, Seamless steel or Copper pipes
Only the green cells and Column "B"
"Velocity" can be edited
Power / Capacity (P) of chiller unit:
P = ρ x Q x C x ΔT
P = Power / Capacity [W]
ρ = Density [kg/m³]
Q = Volumic Flow Rate [m³/s]
C = Specific heat capacity [J/kgK]
ΔT = Temperature difference over chiller/heater [K]
( ρ ) Density
| Water |  |  |  |  | 1 | (x 10³) | kg/m³
| Glycol |  |  |  |  | 1.26 | (x 10³) | kg/m³
Water/glycol mix :
| 20 | % Glycol | 80 | % Water |  | 1.052 | (x 10³) | kg/m³
| ( C )Specific heat capacity | [7 empty] | m³/h | l/h | l/min | l/s
| Water |  |  |  |  | 4.187 | (x 10³) | J/kgK | 100 | 100000 | 1666.6667 | 27.7778
| Glycol |  |  |  |  | 2.43 | (x 10³) | J/kgK | 10 | 10000 | 166.6667 | 2.7778
| Water/glycol mix : | [7 empty] | 99.96 | 99960 | 1666 | 27.7667 | ( ΔT ) Temperature difference over chiller |  |  | 10 | K
| 20 | % Glycol | 80 | % Water |  | 3.8356 | (x 10³) | J/kgK | 999.612 | 999612 | 16660.2 | 277.67
Capacity (P) of chiller unit:
Velocity | aquatherm blue pipe MF |  | aquatherm blue pipe MF |  | Seamless Steel |  | Copper |  | aquatherm blue pipe MF | aquatherm blue pipe MF | Seamless Steel | Copper | aquatherm blue pipe MF | aquatherm blue pipe MF | Seamless Steel | Copper
| SDR7.4/SDR11 |  | SDR17.6 |  | DIN 2448 |  | AS 1432:2000 type B |  | SDR7.4/SDR11 | SDR17.6 | DIN 2448 | AS 1432:2000 type B | SDR7.4/SDR11 | SDR17.6 | DIN 2448 | AS 1432:2000 type B
m/s | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | l/min | l/min | l/min | l/min | kW | kW | kW | kW
0.4 | 20x2.8 | 14.4 |  |  | 21.3x2.0 | 17.3 | 19.1x1.0 | 17.1 | 3.9086 |  | 5.6415 | 5.5118 | 2.6286 |  | 3.7939 | 3.7067
0.6 | 25x3.5 | 18 |  |  | 26.9x2.3 | 22.3 | 25.4x1.2 | 23 | 9.1609 |  | 14.0605 | 14.9571 | 6.1608 |  | 9.4558 | 10.0588
0.8 | 32x2.9 | 26.2 |  |  | 33.7x2.6 | 28.5 | 31.8x1.2 | 29.4 | 25.8782 |  | 30.6211 | 32.5856 | 17.4033 |  | 20.593 | 21.9141
1 | 40x3.7 | 32.6 |  |  | 42.4x2.6 | 37.2 | 38.1x1.2 | 35.7 | 50.0814 |  | 65.2119 | 60.0589 | 33.6802 |  | 43.8556 | 40.3901
1.2 | 50x4.6 | 40.8 |  |  | 48.3x2.6 | 43.1 | 50.8x1.2 | 48.4 | 94.1332 |  | 105.0454 | 132.4686 | 63.3054 |  | 70.6439 | 89.0863
1.4 | 63x5.8 | 51.4 |  |  | 60.3x2.9 | 54.5 | 63.5x1.2 | 61.1 | 174.2992 |  | 195.9576 | 246.2927 | 117.2177 |  | 131.7832 | 165.634
1.5 | 75x6.8 | 61.4 |  |  | 76.1x2.9 | 70.3 | 76.2x1.6 | 73 | 266.4828 |  | 349.3358 | 376.6848 | 179.2119 |  | 234.9313 | 253.3238
1.6 | 90x8.2 | 73.6 |  |  | 88.9x3.2 | 82.5 | 88.9x1.6 | 85.7 | 408.4292 |  | 513.1792 | 553.7615 | 274.6721 |  | 345.1174 | 372.4093
1.7 | 110x10.0 | 90 |  |  | 114.3x3.6 | 107.1 | 101.6x1.6 | 98.4 | 648.896 |  | 918.9016 | 775.6758 | 436.3881 |  | 617.9691 | 521.6486
1.8 | 125x11.4 | 102.2 |  |  | 127.0x4.0 | 119 | 127.0x1.6 | 123.8 | 885.9627 |  | 1201.1785 | 1300.0346 | 595.8175 |  | 807.8028 | 874.2844
1.9 | 160x14.6 | 130.8 | 160x9.1 | 141.8 | 168.3x4.5 | 159.3 | 152.4x2.0 | 148.4 | 1531.8288 | 1800.3096 | 2272.0939 | 1971.7985 | 1030.1679 | 1210.7236 | 1528.0026 | 1326.0513
2 | 200x18.2 | 163.6 | 200x11.4 | 177.2 | 219.1x5.9 | 207.3 | 203.2x2.0 | 199.2 | 2522.5381 | 2959.3652 | 4050.1372 | 3739.8122 | 1696.4284 | 1990.1984 | 2723.7518 | 2515.0556
2.1 | 250x22.7 | 204.6 | 250x14.2 | 221.6 | 273.0x6.3 | 260.4 |  |  | 4142.5875 | 4859.5935 | 6710.3069 |  | 2785.9254 | 3268.1181 | 4512.7387
2.2 | 315x28.6 | 257.8 | 315x17.9 | 279.2 | 323.9x7.1 | 309.7 |  |  | 6890.1653 | 8081.5496 | 9943.659 |  | 4633.6949 | 5434.911 | 6687.1955
2.3 | 355x32.2 | 290.6 | 355x20.1 | 314.8 | 355.6x8.0 | 339.6 |  |  | 9152.931 | 10740.8442 | 12499.8365 |  | 6155.4242 | 7223.3093 | 8406.2467
2.4 | 400x36.3 | 327.6 | 400x22.7 | 354.6 | 406.4x8.8 | 388.8 |  |  | 12137.8051 | 14220.9902 | 17096.4085 |  | 8162.7775 | 9563.7372 | 11497.4806
2.5 | 450x40.9 | 368.2 | 450x25.5 | 399 | 457.0x10.0 | 437 |  |  | 15971.6104 | 18755.426 | 22498.0053 |  | 10741.0443 | 12613.184 | 15130.1005
2.6 |  |  | 500x28.4 | 443.2 | 508.0x11.0 | 486 |  |  |  | 24066.5581 | 28939.2331 |  |  | 16184.9657 | 19461.8812
2.8 |  |  | 560x31.7 | 496.6 | 559.0x12.5 | 534 |  |  |  | 32539.6287 | 37625.4478 |  |  | 21883.178 | 25303.4347
3 |  |  | 630x35.7 | 558.6 | 610.0x12.5 | 585 |  |  |  | 44112.7618 | 48380.9196 |  |  | 29666.2088 | 32536.5813
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on B37: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)

## Capacity by flow rate
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
Capacity of chiller units (secondary refrigeration systems)
in combination with
aquatherm blue pipe SDR7.4 /SDR11/SDR17.6 MF, Seamless steel or Copper pipes
Only the green cells
can be edited
Power / Capacity (P) of chiller unit:
P = ρ x Q x C x ΔT
P = Power / Capacity [W]
ρ = Density [kg/m³]
Q = Volumic Flow Rate [m³/s]
C = Specific heat capacity [J/kgK]
ΔT = Temperature difference over chiller/heater [K]
( ρ ) Density
| Water |  |  |  |  | 1 | (x 10³) | kg/m³
| Glycol |  |  |  |  | 1.26 | (x 10³) | kg/m³
Water/glycol mix :
| 10 | % Glycol | 90 | % Water |  | 1.026 | (x 10³) | kg/m³
( C )Specific heat capacity
| Water |  |  |  |  | 4.187 | (x 10³) | J/kgK
| Glycol |  |  |  |  | 2.43 | (x 10³) | J/kgK | m³/h | l/h | l/min | l/s
| Water/glycol mix : | [7 empty] | 100 | 100000 | 1666.6667 | 27.7778
| 10 | % Glycol | 90 | % Water |  | 4.0113 | (x 10³) | J/kgK | 10 | 10000 | 166.6667 | 2.7778
[9 empty] | 6.72 | 6720 | 112 | 1.8667
| ( ΔT ) Temperature difference over chiller | [5 empty] | 5 | K | 999.612 | 999612 | 16660.2 | 277.67
Flow Rate | aquatherm blue pipe MF |  | aquatherm blue pipe MF |  | Seamless Steel |  | Copper |  | aquatherm blue pipe MF | aquatherm blue pipe MF | Seamless Steel | Copper | Capacity (P) of chiller unit:
| SDR7.4/SDR11 |  | SDR17.6 |  | DIN 2448 |  | AS 1432:2000 type B |  | SDR7.4/SDR11 | SDR17.6 | DIN 2448 | AS 1432:2000 type B
l/min | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | m/s | m/s | m/s | m/s | kW
5 | 20x2.8 | 14.4 |  |  | 21.3x2.0 | 17.3 | 19.1x1.0 | 17.1 | 0.51169 |  | 0.35452 | 0.36286 | 1.7148
12 | 25x3.5 | 18 |  |  | 26.9x2.3 | 22.3 | 25.4x1.2 | 23 | 0.78595 |  | 0.51207 | 0.48138 | 4.1156
112 | 32x2.9 | 26.2 |  |  | 33.7x2.6 | 28.5 | 31.8x1.2 | 29.4 | 3.4624 |  | 2.9261 | 2.7497 | 38.4122
112 | 40x3.7 | 32.6 |  |  | 42.4x2.6 | 37.2 | 38.1x1.2 | 35.7 | 2.2364 |  | 1.7175 | 1.8648 | 38.4122
112 | 50x4.6 | 40.8 |  |  | 48.3x2.6 | 43.1 | 50.8x1.2 | 48.4 | 1.4278 |  | 1.2794 | 1.0146 | 38.4122
112 | 63x5.8 | 51.4 |  |  | 60.3x2.9 | 54.5 | 63.5x1.2 | 61.1 | 0.8996 |  | 0.80017 | 0.63664 | 38.4122
112 | 75x6.8 | 61.4 |  |  | 76.1x2.9 | 70.3 | 76.2x1.6 | 73 | 0.63043 |  | 0.48091 | 0.446 | 38.4122
112 | 90x8.2 | 73.6 |  |  | 88.9x3.2 | 82.5 | 88.9x1.6 | 85.7 | 0.43875 |  | 0.3492 | 0.32361 | 38.4122
112 | 110x10.0 | 90 |  |  | 114.3x3.6 | 107.1 | 101.6x1.6 | 98.4 | 0.29342 |  | 0.2072 | 0.24546 | 38.4122
112 | 125x11.4 | 102.2 |  |  | 127.0x4.0 | 119 | 127.0x1.6 | 123.8 | 0.22755 |  | 0.16784 | 0.15507 | 38.4122
112 | 160x14.6 | 130.8 | 160x9.1 | 141.8 | 168.3x4.5 | 159.3 | 152.4x2.0 | 148.4 | 0.13892 | 0.1182 | 0.093658 | 0.10792 | 38.4122
112 | 200x18.2 | 163.6 | 200x11.4 | 177.2 | 219.1x5.9 | 207.3 | 203.2x2.0 | 199.2 | 0.088799 | 0.075692 | 0.055307 | 0.059896 | 38.4122
112 | 250x22.7 | 204.6 | 250x14.2 | 221.6 | 273.0x6.3 | 260.4 |  |  | 0.056776 | 0.048399 | 0.035051 |  | 38.4122
112 | 315x28.6 | 257.8 | 315x17.9 | 279.2 | 323.9x7.1 | 309.7 |  |  | 0.035761 | 0.030489 | 0.02478 |  | 38.4122
5100 | 355x32.2 | 290.6 | 355x20.1 | 314.8 | 355.6x8.0 | 339.6 |  |  | 1.2816 | 1.0921 | 0.93841 |  | 1749.1274
400 | 400x36.3 | 327.6 | 400x22.7 | 354.6 | 406.4x8.8 | 388.8 |  |  | 0.079092 | 0.067506 | 0.056152 |  | 137.1865
112 | 450x40.9 | 368.2 | 450x25.5 | 399 | 457.0x10.0 | 437 |  |  | 0.017531 | 0.014929 | 0.012446 |  | 38.4122
112 |  |  | 500x28.4 | 443.2 | 508.0x11.0 | 486 |  |  |  | 0.0121 | 0.010062 |  | 38.4122
112 |  |  | 560x31.7 | 496.6 | 559.0x12.5 | 534 |  |  |  | 0.0096375 | 0.0083348 |  | 38.4122
112 |  |  | 630x35.7 | 558.6 | 610.0x12.5 | 585 |  |  |  | 0.0076168 | 0.0069449 |  | 38.4122
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on L41: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)
Note on M41: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)
Note on N41: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)
Note on O41: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)