## Energy Savings
Aquatherm Australia Pty Limited
Ecological pipe systems: just say yes to a better world!
Energy cost (savings) for Hot potable Water Reticulation Systems (HWRS)
(Energy costs based on gas fired hot water units with a 100% efficiency)
Calculation conditions:
Q = Øm x Cw x ΔT
Q = Energy required [kW]
Øm = Mass flow rate [kg/s] or Volume flow rate [l/s] x density [1 kg/ltr. water]
| Cw = Specific heat capacity of water. | 4.187 | kJ/kgK
(to heat up 1 kg (litre) of water by 1°C (1K) you require 4,187 kJ of energy.)
ΔT = Required hot water flow temperature - cold water mains temperature.
Energy cost based on gas fired hot water units (with a 100% efficiency)
1 Nm3 of natural gas provides approx. 10.83 kWh or 39 MJ of energy.
| Average current gas price per MJ (= 0.278 kWh) | 0.04
| Average price per 1 kWh based on current gas price | 0.14388
| Case 1 (flow water at high temperature) |  |  | Case 2 (flow water at low temperature)
| Only the green cells can be amended |  |  | Only the green cells can be amended
| Required warm water temperature at tap | 50 | °C | Required warm water temperature at tap | 50 | °C
| Warm water demand | 9.13 | l/s | Warm water demand | 9.13 | l/s
| Hours of warm water demand per day | 1 | hour(s) | Hours of warm water demand per day | 1 | hour(s)
| Hot water temperature set at hot water unit(s) | 70 | °C | Hot water temperature set at hot water unit(s) | 65 | °C
| Mains cold water temperature | 15 | °C | Mains cold water temperature | 15 | °C
| Required hot water flow rate | 5.81 | l/s | Required hot water flow rate | 6.391 | l/s
| Required cold water flow rate | 3.32 | l/s | Required cold water flow rate | 2.739 | l/s
| Energy required per day | 1337.9559 | kWh | Energy required per day | 1337.9559 | kWh
| Energy Cost per day (based on current gas price) | 192.5116 |  | Energy Cost per day (based on current gas price) | 192.5116
| Energy Cost per year (based on current gas price) | 70266.7461 |  | Energy Cost per year (based on current gas price) | 70266.7461
| Energy Savings per year |  |  | 0
(= excl. the cost savings due to the lower heat loss [kWh], when conveying hot potable water through the pipe system at a lower hot water temperature).
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Australia Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
Aquatherm Australia Pty Limited
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on C25: https://www.convert-me.com/en/convert/energy/cmsgas.html?u=cmsgas&v=1
Note on C26: https://secure.energyaustralia.com.au/EnergyPriceFactSheets/Docs/EPFS/PriceFactSheet_ENE390963SR.pdf
Note on D35: DN100 Copper Type B Velocity 1.2 m/s
Note on H35: DN100 Copper Type B Velocity 1.2 m/s

## Sheet2
1 | 5855.5622 | 1 | 5855.5622
2 | 11711.1243 | 2 | 11711.1243
3 | 17566.6865 | 3 | 17566.6865
4 | 23422.2487 | 4 | 23422.2487
5 | 29277.8109 | 5 | 29277.8109
6 | 35133.373 | 6 | 35133.373
7 | 40988.9352 | 7 | 40988.9352
8 | 46844.4974 | 8 | 46844.4974
9 | 52700.0596 | 9 | 52700.0596
10 | 58555.6217 | 10 | 58555.6217
11 | 64411.1839 | 11 | 64411.1839
12 | 70266.7461 | 12 | 70266.7461