## Pressure loss
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
Friction Head Loss in water pipes according to Hazen-Williams formula
aquatherm green pipe SDR11 S, aquatherm green pipe SDR7.4 MF, aquatherm blue pipe SDR7.4 /SDR11/SDR17.6 MF,
aquatherm red pipe SDR7.4 MF HI, Seamless Carbon Steel DIN 2448 and Copper AS 1432 : 2000 type B pipes
Only the green cells and Column "B"
"Velocity" can be edited
The Hazen-Williams Formula:
Q = Flow rate [l/min]
C = Hazen-Williams coefficient (determinated for the type of pipe material)
(based on "normal" condition with approximately 1 m/s).
d = inside hydraulic diameter (dh) [mm]
Note that the Hazen-Williams formula is empirical and lacks a theoretical basis
The Hazen-Williams formula gives accurate friction head loss for fluids with kinematic viscosity
of approximately 1.1 cSt (water at approx. 20⁰ C). (1 cSt (centiStokes) = 10-6 m2/s)
For hot water with a lower kinematic viscosity (0.55 cSt at 130⁰F (54.4⁰C)) the error will be significant.
(The results for the formula is acceptable for cold water at 60oF (15.6oC) with kinematic viscosity 1.13 cSt. )
The Hazen Williams method is only valid for water flowing at ordinary temperatures between 40 ⁰F (4.44 ⁰C) to 75 ⁰F (23.89 ⁰C)
Source: www.EngineeringToolBox.com
| Water temperature correction: | [11 empty] | kPa | mbar | mmH₂O | mmHg | psi | kg/cm²
[13 empty] | 100 | 1000 | 10196.9999 | 752.5461 | 14.5 | 1.0197
|  | Water temperature: |  | 20 | °C |  | min. 4°C and max. 30°C due to accuracy | [5 empty] | 1000 | 10000 | 101969.9992 | 7525.4612 | 145 | 10.197
[7 empty] | of the Hazen-Williams formula | [5 empty] | 19.6136 | 196.1361 | 2000 | 147.6015 | 2.844 | 0.2
[9 empty] | 1 |  |  |  | 1328.8222 | 13288.2221 | 135500 | 10000 | 192.6782 | 13.5499
|  |  |  | Only the green cells can be edited | [8 empty] | 689.6587 | 6896.5873 | 70324.137 | 5190 | 100 | 7.0324
[13 empty] | 2000 | 20000 | 203941.0473 | 15050.9998 | 290 | 20.394
Flow Rate | aquatherm green pipe |  | green pipe / | red pipe | aquatherm blue pipe |  | aquatherm blue pipe |  | Seamless Steel |  | Copper |  | aquatherm green pipe | green pipe / red pipe | aquatherm blue pipe | aquatherm blue pipe | Seamless Steel | Copper
| SDR11 S |  | SDR7.4 MF |  | SDR7.4/SDR11 MF |  | SDR17.6 MF |  | DIN 2448 |  | AS 1432:2000 type B |  | SDR11 S | SDR7.4 MF | SDR7.4/SDR11 MF | SDR17.6 MF | DIN 2448 | AS 1432:2000 type B
l/min | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | kPa/m | kPa/m | kPa/m | kPa/m | kPa/m | kPa/m
840 | 20x1.9 | 16.2 | 20x2.8 | 14.4 | 20x2.8 | 14.4 |  |  | 21.3x2.0 | 17.3 | 19.1x1.0 | 17.1 | 1886.1017 | 3347.1709 | 3347.1709 |  | 2899.9301 | 1888.7992
840 | 25x2.3 | 20.4 | 25x3.5 | 18 | 25x3.5 | 18 |  |  | 26.9x2.3 | 22.3 | 25.4x1.2 | 23 | 613.7681 | 1129.0837 | 1129.0837 |  | 842.2235 | 445.9255
840 | 32x2.9 | 26.2 | 32x4.4 | 23.2 | 32x2.9 | 26.2 |  |  | 33.7x2.6 | 28.5 | 31.8x1.2 | 29.4 | 181.4579 | 328.0777 | 181.4579 |  | 255.022 | 134.9042
840 | 40x3.7 | 32.6 | 40x5.5 | 29 | 40x3.7 | 32.6 |  |  | 42.4x2.6 | 37.2 | 38.1x1.2 | 35.7 | 62.5941 | 110.6687 | 62.5941 |  | 69.6832 | 52.4062
840 | 50x4.6 | 40.8 | 50x6.9 | 36.2 | 50x4.6 | 40.8 |  |  | 48.3x2.6 | 43.1 | 50.8x1.2 | 48.4 | 20.9888 | 37.5831 | 20.9888 |  | 34.0226 | 11.9036
840 | 63x5.8 | 51.4 | 63x8.6 | 45.8 | 63x5.8 | 51.4 |  |  | 60.3x2.9 | 54.5 | 63.5x1.2 | 61.1 | 6.8157 | 11.9533 | 6.8157 |  | 10.8498 | 3.827
840 | 75x6.8 | 61.4 | 75x10.3 | 54.4 | 75x6.8 | 61.4 |  |  | 76.1x2.9 | 70.3 | 76.2x1.6 | 73 | 2.8676 | 5.1705 | 2.8676 |  | 3.1405 | 1.6088
840 | 90x8.2 | 73.6 | 90x12.3 | 65.4 | 90x8.2 | 73.6 |  |  | 88.9x3.2 | 82.5 | 88.9x1.6 | 85.7 | 1.1863 | 2.1088 | 1.1863 |  | 1.4406 | 0.73665
900 | 110x10.0 | 90 | 110x15.1 | 79.8 | 110x10.0 | 90 |  |  | 114.3x3.6 | 107.1 | 101.6x1.6 | 98.4 | 0.50603 | 0.90904 | 0.50603 |  | 0.45923 | 0.42699
900 | 125x11.4 | 102.2 | 125x17.1 | 90.8 | 125x11.4 | 102.2 |  |  | 127.0x4.0 | 119 | 127.0x1.6 | 123.8 | 0.27246 | 0.48468 | 0.27246 |  | 0.27491 | 0.13956
900 | 160x14.6 | 130.8 | 160x21.9 | 116.2 | 160x14.6 | 130.8 | 160x9.1 | 141.8 | 168.3x4.5 | 159.3 | 152.4x2.0 | 148.4 | 0.081932 | 0.14581 | 0.081932 | 0.055293 | 0.066422 | 0.057733
840 | 200x18.2 | 163.6 | 200x27.4 | 145.2 | 200x18.2 | 163.6 | 200x11.4 | 177.2 | 219.1x5.9 | 207.3 | 203.2x2.0 | 199.2 | 0.024254 | 0.043364 | 0.024254 | 0.016439 | 0.016212 | 0.012115
840 | 250x22.7 | 204.6 | 250x34.2 | 181.6 | 250x22.7 | 204.6 | 250x14.2 | 221.6 | 273.0x6.3 | 260.4 |  |  | 0.0081619 | 0.014588 | 0.0081619 | 0.0055332 | 0.0053395
840 | 315x28.6 | 257.8 | 315x42.6 | 229.8 | 315x28.6 | 257.8 | 315x17.9 | 279.2 | 323.9x7.1 | 309.7 |  |  | 0.0026482 | 0.0046358 | 0.0026482 | 0.001796 | 0.002295
840 | 355x32.2 | 290.6 | 355x48.0 | 259 | 355x32.2 | 290.6 | 355x20.1 | 314.8 | 355.6x8.0 | 339.6 |  |  | 0.0014779 | 0.002589 | 0.0014779 | 0.0010011 | 0.0014651
840 | 400x36.3 | 327.6 |  |  | 400x36.3 | 327.6 | 400x22.7 | 354.6 | 406.4x8.8 | 388.8 |  |  | 0.00082448 |  | 0.00082448 | 0.00056063 | 0.00075806
840 | 450x40.9 | 368.2 |  |  | 450x40.9 | 368.2 | 450x25.5 | 399 | 457.0x10.0 | 437 |  |  | 0.00046674 |  | 0.00046674 | 0.00031562 | 0.00042907
840 | [6 empty] | 500x28.4 | 443.2 | 508.0x11.0 | 486 | [5 empty] | 0.00018922 | 0.00025571
840 | [6 empty] | 560x31.7 | 496.6 | 559.0x12.5 | 534 | [5 empty] | 0.00010873 | 0.00016164
840 | [6 empty] | 630x35.7 | 558.6 | 610.0x12.5 | 585 | [5 empty] | 6.1309e-05 | 0.00010366
| C = Hazen-Williams coefficient | [11 empty] | Friction head loss for other pipe materials
| aquatherm green pipe (MF) / aquatherm blue pipe MF / aquatherm red pipe MF HI | [7 empty] | C = | 150
| Steel, welded and seamless | [7 empty] | C = | 100 |  |  |  | The Hazen-Williams Formula:
| Copper | [7 empty] | C = | 130
| ABS - Acrylonite Butadiene Styrene | [7 empty] | C = | 130 | [6 empty] | Water temperature [⁰C]:
| Aluminum | [7 empty] | C = | 130 | [6 empty] | 20
| Asbestos cement | [7 empty] | C = | 140
| Asphalt lining | [7 empty] | C = | 130
| Brass | [7 empty] | C = | 130 |  |  | Flow Rate | C-factor | dh | Pipe length | Velocity | Friction head loss
| Brick sewer | [7 empty] | C = | 90 |  |  | l/min |  | [mm] | [m] | [m/s] | kPa
| Cast-Iron - new unlined (CIP) | [7 empty] | C = | 130 |  |  | 200 | 100 | 100 | 500 | 0.42441 | 19.8441
| Cast-Iron 10 years old | [7 empty] | C = | 107
| Cast-Iron 20 years old | [7 empty] | C = | 89 |  |  | Pump capacity:
| Cast-Iron 30 years old | [7 empty] | C = | 75
| Cast-Iron 40 years old | [7 empty] | C = | 64 |  |  | P = q x p | P = capacity [W]
| Cast-Iron, asphalt coated | [7 empty] | C = | 100 |  |  |  | q = flow capacity [m³/s]
| Cast-Iron, cement lined | [7 empty] | C = | 140 |  |  |  | p = pressure [Pa] (static + dynamic water pressure + friction head loss in pipes)
| Cast-Iron, bituminous lined | [7 empty] | C = | 140
| Cast-Iron, sea-coated | [7 empty] | C = | 120 |  |  | The lower the Hazen-Williams coefficient, the less energy is needed to pump
| Cast-Iron, wrought plain | [7 empty] | C = | 100 |  |  | around the same amount of water (flow capacity), with the same pressure
| Cement lining | [7 empty] | C = | 130 |  |  | through the same inner pipe diameter!
| Concrete | [7 empty] | C = | 100
| Corrugated Metal | [7 empty] | C = | 60 |  |  | By using aquatherm PP-R pipes, instead of metal pipes,
| Ductile Iron Pipe (DIP) | [7 empty] | C = | 140 |  |  | you are lowering your Carbon Footprint!
| Ductile Iron, cement lined | [7 empty] | C = | 120
| Fiber | [7 empty] | C = | 140 |  |  | m³/h | l/h | l/min | l/s
| Fiber Glass Pipe - FRP | [7 empty] | C = | 150 |  |  | 100 | 100000 | 1666.6667 | 27.7778
| Galvanized iron | [7 empty] | C = | 120 |  |  | 10 | 10000 | 166.6667 | 2.7778
| Glass | [7 empty] | C = | 130 |  |  | 99.96 | 99960 | 1666 | 27.7667
| Lead | [7 empty] | C = | 130 |  |  | 999.612 | 999612 | 16660.2 | 277.67
| Polyethylene, PE, PEH | [7 empty] | C = | 140
| Polyvinyl chloride, PVC, CPVC | [7 empty] | C = | 150 |  |  | kPa | mbar | mmH₂O | mmHg | psi | kg/cm²
| Steel new unlined | [7 empty] | C = | 140 |  |  | 0.96 | 9.6 | 97.8912 | 7.2244 | 0.1392 | 0.0097891
| Steel, corrugated | [7 empty] | C = | 60 |  |  | 2000 | 20000 | 203939.9984 | 15050.9224 | 290 | 20.394
| Steel, interior riveted, no projecting rivets | [7 empty] | C = | 110 |  |  | 2000 | 20000.0002 | 203940 | 15050.9225 | 290 | 20.394
| Steel, vitrified, spiral-riveted | [7 empty] | C = | 90 |  |  | 1999.997 | 19999.9702 | 203939.695 | 15050.9 | 289.9981 | 20.3939
| Tin | [7 empty] | C = | 130 |  |  | 2000.0103 | 20000.1031 | 203939.9973 | 15051 | 290 | 20.394
| Vitrified Clay | [7 empty] | C = | 110 |  |  | 2000 | 20000 | 203941.0473 | 15050.9998 | 290 | 20.394
Source: www.EngineeringToolBox.com
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on P42: Hazen-Williams C-factor, see cell L67
Note on Q42: Hazen-Williams C-factor, see cell L67
Note on R42: Hazen-Williams C-factor, see cell L67
Note on S42: Hazen-Williams C-factor, see cell L67
Note on T42: Hazen-Williams C-factor, see cell L68
Note on U42: Hazen-Williams C-factor, see cell L69
Note on Q74: See cell L67 - cell L103
Note on T74: Max. 3.0 m/s as per AS 3500 and max. 1.5 m/s for aquatherm green pipe MF.
Note on U74: Is including temperature correction (cell F35)

## Flow Rate to Velocity
[14 empty] | m³/h | l/h | l/min | l/s
|  |  |  | Flow Rate [l/min] => Velocity [m/s] | [9 empty] | 50 | 50000 | 833.3333 | 13.8889
[14 empty] | 10 | 10000 | 166.6667 | 2.7778
[6 empty] | Only the green cells can be edited | [7 empty] | 99.96 | 99960 | 1666 | 27.7667
[14 empty] | 999.612 | 999612 | 16660.2 | 277.67
Flow Rate | aquatherm green pipe |  | green pipe | red pipe | aquatherm blue pipe |  | aquatherm blue pipe |  | Seamless Steel |  | Copper |  | aquatherm green pipe | green pipe / red pipe | aquatherm blue pipe | aquatherm blue pipe | Seamless Steel | Copper
| SDR11 S |  | SDR7.4 MF |  | SDR7.4/SDR11 MF |  | SDR17.6 MF |  | DIN 2448 |  | AS 1432:2000 type B |  | SDR11 S | SDR7.4 MF | SDR7.4/SDR11 MF | SDR17.6 MF | DIN 2448 | AS 1432:2000 type B
l/min | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | m/s | m/s | m/s | m/s | m/s | m/s
840 | 20x1.9 | 16.2 | 20x2.8 | 14.4 | 20x2.8 | 14.4 |  |  | 21.3x2.0 | 17.3 | 19.1x1.0 | 17.1 | 67.9216 | 85.9633 | 85.9633 |  | 59.5588 | 60.9601
840 | 25x2.3 | 20.4 | 25x3.5 | 18 | 25x3.5 | 18 |  |  | 26.9x2.3 | 22.3 | 25.4x1.2 | 23 | 42.8329 | 55.0165 | 55.0165 |  | 35.845 | 33.6963
840 | 32x2.9 | 26.2 | 32x4.4 | 23.2 | 32x2.9 | 26.2 |  |  | 33.7x2.6 | 28.5 | 31.8x1.2 | 29.4 | 25.9678 | 33.1179 | 25.9678 |  | 21.9456 | 20.6226
840 | 40x3.7 | 32.6 | 40x5.5 | 29 | 40x3.7 | 32.6 |  |  | 42.4x2.6 | 37.2 | 38.1x1.2 | 35.7 | 16.7727 | 21.1954 | 16.7727 |  | 12.8811 | 13.9863
840 | 50x4.6 | 40.8 | 50x6.9 | 36.2 | 50x4.6 | 40.8 |  |  | 48.3x2.6 | 43.1 | 50.8x1.2 | 48.4 | 10.7082 | 13.6026 | 10.7082 |  | 9.5959 | 7.6093
840 | 63x5.8 | 51.4 | 63x8.6 | 45.8 | 63x5.8 | 51.4 |  |  | 60.3x2.9 | 54.5 | 63.5x1.2 | 61.1 | 6.747 | 8.4978 | 6.747 |  | 6.0013 | 4.7748
840 | 75x6.8 | 61.4 | 75x10.3 | 54.4 | 75x6.8 | 61.4 |  |  | 76.1x2.9 | 70.3 | 76.2x1.6 | 73 | 4.7283 | 6.0234 | 4.7283 |  | 3.6068 | 3.345
840 | 90x8.2 | 73.6 | 90x12.3 | 65.4 | 90x8.2 | 73.6 |  |  | 88.9x3.2 | 82.5 | 88.9x1.6 | 85.7 | 3.2907 | 4.1676 | 3.2907 |  | 2.619 | 2.427
900 | 110x10.0 | 90 | 110x15.1 | 79.8 | 110x10.0 | 90 |  |  | 114.3x3.6 | 107.1 | 101.6x1.6 | 98.4 | 2.3579 | 2.9991 | 2.3579 |  | 1.665 | 1.9725
900 | 125x11.4 | 102.2 | 125x17.1 | 90.8 | 125x11.4 | 102.2 |  |  | 127.0x4.0 | 119 | 127.0x1.6 | 123.8 | 1.8285 | 2.3165 | 1.8285 |  | 1.3487 | 1.2461
900 | 160x14.6 | 130.8 | 160x21.9 | 116.2 | 160x14.6 | 130.8 | 160x9.1 | 141.8 | 168.3x4.5 | 159.3 | 152.4x2.0 | 148.4 | 1.1163 | 1.4145 | 1.1163 | 0.94984 | 0.75261 | 0.86723
840 | 200x18.2 | 163.6 | 200x27.4 | 145.2 | 200x18.2 | 163.6 | 200x11.4 | 177.2 | 219.1x5.9 | 207.3 | 203.2x2.0 | 199.2 | 0.666 | 0.84548 | 0.666 | 0.56769 | 0.4148 | 0.44922
840 | 250x22.7 | 204.6 | 250x34.2 | 181.6 | 250x22.7 | 204.6 | 250x14.2 | 221.6 | 273.0x6.3 | 260.4 |  |  | 0.42582 | 0.54051 | 0.42582 | 0.36299 | 0.26288
840 | 315x28.6 | 257.8 | 315x42.6 | 229.8 | 315x28.6 | 257.8 | 315x17.9 | 279.2 | 323.9x7.1 | 309.7 |  |  | 0.26821 | 0.33755 | 0.26821 | 0.22867 | 0.18585
840 | 355x32.2 | 290.6 | 355x48.0 | 259 | 355x32.2 | 290.6 | 355x20.1 | 314.8 | 355.6x8.0 | 339.6 |  |  | 0.21108 | 0.26573 | 0.21108 | 0.17987 | 0.15456
840 | 400x36.3 | 327.6 |  |  | 400x36.3 | 327.6 | 400x22.7 | 354.6 | 406.4x8.8 | 388.8 |  |  | 0.16609 |  | 0.16609 | 0.14176 | 0.11792
840 | 450x40.9 | 368.2 |  |  | 450x40.9 | 368.2 | 450x25.5 | 399 | 457.0x10.0 | 437 |  |  | 0.13148 |  | 0.13148 | 0.11197 | 0.093342
840 | [6 empty] | 500x28.4 | 443.2 | 508.0x11.0 | 486 | [5 empty] | 0.090748 | 0.075468
840 | [6 empty] | 560x31.7 | 496.6 | 559.0x12.5 | 534 | [5 empty] | 0.072281 | 0.062511
840 | [6 empty] | 630x35.7 | 558.6 | 610.0x12.5 | 585 | [5 empty] | 0.057126 | 0.052087