## Linear expansion forces
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
Calculational determination of linear expansion forces of
aquatherm green pipe SDR7.4 MF and aquatherm blue pipes SDR7.4 MF / SDR11 MF and SDR17.6 MF.
Only the green cells can be edited
In the following green cells you can specify the values that apply for your system.
You can only choose from the pipe diameters available in the specific pipe type.
The aquatherm green pipes MF and the aquatherm blue pipes MF have a permissible processing temperature of -10°C up to +50°C (excl. electrofusion sockets; +5°C up to +40°C).
Only these permissible processing temperatures can be filled in.
The aquatherm green pipes MF and the aquatherm blue pipes MF have a permissible working temperature of -20°C up to +90°C.
Only these permissible working temperatures can be filled in.
The linear expansion forces [F] of the aquatherm green pipes MF and the aquatherm blue pipes MF can be calculated by Hooke's law.
F = A x α x E x ΔT (= Hooke's law)
[A] is the cross-sectional area of the pipe.
The linear expansion coefficient of the aquatherm PP-R MF pipes [α] is 0.035 mm/mK (at 23⁰C).
To calculate the linear expansion forces of the aquatherm PP-R MF pipes, a constant modulus of elasticity [E] of 1200 N/mm² or 1.2 GPa (at 23⁰C) is used.
ΔT = Difference between the avarage pipe wall temperature during operation and temperature during processing.
We use the "English method" because the temperature is variable through the plastic pipe wall. We also calculate the influence of the ambient temperature.
ΔT ("English method") = 0.65 x ΔT (inside pipe) + 0.1 x ΔT (outside pipe)
Negative reaction forces [F] mean contraction of the pipe, positive reaction forces [F] mean expansion of the pipe.
aquatherm green pipe |  |  | Ambient Temperature (outside pipe) |  | Medium Temperature (inside pipe) |  |  |  | Weight
SDR7.4 MF | Pipe |  | Temperature during | Temperature during | Temperature during | Medium Temperature | Reaction Force |  | Pipe | Water
diameter | dimensions | DN | processing | operation | processing / filling | during operation |  | Reaction Force | only | content
[mm] | [mm] | [mm] | [°C] | [°C] | [°C] | [°C] | Newton [N] | kilogram-force [kgf] | kg/meter | liters/kg per meter
110 | 110x15,1 | 80 | 5 | 22.5 | 6.5 | 90 | 10593 | 1079.8165 | 4.576 | 4.999
aquatherm blue pipe |  |  | Ambient Temperature (outside pipe) |  | Medium Temperature (inside pipe) |  |  |  | Weight
SDR7.4 MF / SDR11 MF | Pipe |  | Temperature during | Temperature during | Temperature during | Medium Temperature |  |  | Pipe | Water
diameter | dimensions | DN | processing | operation | processing / filling | during operation | Reaction Force | Reaction Force | only | content
[mm] | [mm] | [mm] | [°C] | [°C] | [°C] | [°C] | Newton [N] | kilogram-force [kgf] | kg/meter | liters/kg per meter
250 | 250x22,7 | 200 | 5 | 20 | 40 | 20 | -7829 | -798.0632 | 16.3 | 32.861
aquatherm blue pipe |  |  | Ambient Temperature (outside pipe) |  | Medium Temperature (inside pipe) |  |  |  | Weight
SDR17.6 MF | Pipe |  | Temperature during | Temperature during | Temperature during | Medium Temperature |  |  | Pipe | Water
diameter | dimensions | DN | processing | operation | processing / filling | during operation | Reaction Force | Reaction Force | only | content
[mm] | [mm] | [mm] | [°C] | [°C] | [°C] | [°C] | Newton [N] | kilogram-force [kgf] | kg/meter | liters/kg per meter
315 | 315x17,9 | 300 | 10 | 30 | 5 | 12 | 4596 | 468.5015 | 16.735 | 61.223
To calculate the linear expansion, bending sides and/or expansion loops, please ask for the Aquatherm linear expansion calculation (Excel).
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au

## Calculation
Linear expansion forces Fusiotherm Faser SDR7.4
Pipe diameter [mm] | Wall thickness [mm] | [DN] | Bore [mm] | Area [mm²] | Ambient Temp during processing [° C] | Ambient Temp during operation [° C] | Medium Temp during processing [° C] | Medium Temp during operation [° C] | ΔT [°C] | E modulus [N/mm²] | α (Uitzettingscoeff.) [mm/°C*m] | F (Reaktion Force) [N] | F (Reaktion Force) [kgf] | Weight pipe | Weight water content
|  |  |  | afronden((3,14/4)*(A5^2-(A5-2*B5)^2);1 |  |  |  |  | 0.1*(G5-F5)+0.65*(I5-H5) |  |  | afronden((E5*J5*K5*(L5/1000));1 | M5/9,81 | kg / m | kg / m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
20 | 2.8 | 15 | 20x2,8 | 151.3 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 356 | 36.2895 | 0.158 | 0.163
25 | 3.5 | 20 | 25x3,5 | 236.4 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 556 | 56.6769 | 0.246 | 0.254
32 | 4.4 | 25 | 32x4,4 | 381.5 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 898 | 91.5392 | 0.394 | 0.423
40 | 5.5 | 32 | 40x5,5 | 596.1 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 1403 | 143.0173 | 0.613 | 0.66
50 | 6.9 | 40 | 50x6,9 | 934.3 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 2198 | 224.0571 | 0.955 | 1.029
63 | 8.6 | 50 | 63x8,6 | 1469.8 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 3459 | 352.5994 | 1.5 | 1.647
75 | 10.3 | 50 | 75x10,3 | 2093.6 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 4926 | 502.1407 | 2.135 | 2.323
90 | 12.3 | 65 | 90x12,3 | 3002.5 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 7065 | 720.1835 | 3.058 | 3.358
110 | 15.1 | 80 | 110x15,1 | 4501.9 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 10593 | 1079.8165 | 4.576 | 4.999
125 | 17.1 | 90 | 125x17,1 | 5796.5 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 13639 | 1390.316 | 5.891 | 6.472
160 | 21.9 | 125 | 160x21,9 | 9501.4 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 22357 | 2279.001 | 9.538 | 10.599
200 | 27.4 | 150 | 200x27,4 | 14857.4 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 34960 | 3563.7105 | 15.051 | 16.558
250 | 34.2 | 175 | 250x34,2 | 23186.1 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 54558 | 5561.4679 | 23.479 | 25.901
315 | 42.6 | 225 | 315x42,6 | 36455.9 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 85783 | 8744.4444 | 36.916 | 41.475
355 | 48 | 250 | 355x48,0 | 46294.6 | 5 | 22.5 | 6.5 | 90 | 56.025 | 1200 | 0.035 | 108934 | 11104.3833 | 46.879 | 52.685
Linear expansion forces Climatherm Faser SDR7.4/SDR11
Pipe diameter [mm] | Wall thickness [mm] | [DN] | Bore [mm] | Area [mm²] | Ambient Temp during processing [° C] | Ambient Temp during operation [° C] | Medium Temp during processing [° C] | Medium Temp during operation [° C] | ΔT [°C] | E modulus [N/mm²] | α (Uitzettingscoeff.) [mm/°C*m] | F (Reaktion Force) [N] | F (Reaktion Force) [kgf] | Weight pipe | Weight water content
|  |  |  | afronden((3,14/4)*(A5^2-(A5-2*B5)^2);1 |  |  |  |  | 0.1*(G5-F5)+0.65*(I5-H5) |  |  | afronden((E5*J5*K5*(L5/1000));1 | M5/9,81 | kg / m | kg / m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
20 | 2.8 | 15 | 20x2,8 | 151.3 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -73 | -7.4414 | 0.159 | 0.163
25 | 3.5 | 20 | 25x3,5 | 236.4 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -114 | -11.6208 | 0.248 | 0.254
32 | 2.9 | 25 | 32x2,9 | 265.1 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -128 | -13.0479 | 0.281 | 0.539
40 | 3.7 | 32 | 40x3,7 | 421.9 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -204 | -20.7951 | 0.435 | 0.834
50 | 4.6 | 40 | 50x4,6 | 656.1 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -317 | -32.314 | 0.675 | 1.307
63 | 5.8 | 50 | 63x5,8 | 1042.3 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -503 | -51.2742 | 1.065 | 2.074
75 | 6.9 | 65 | 75x6,9 | 1476.2 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -713 | -72.6809 | 1.482 | 2.959
90 | 8.2 | 80 | 90x8,2 | 2107.3 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -1018 | -103.7717 | 2.145 | 4.252
110 | 10 | 100 | 110x10 | 3141.6 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -1517 | -154.6381 | 3.175 | 6.359
125 | 11.4 | 125 | 125x11,4 | 4068.5 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -1965 | -200.3058 | 4.118 | 8.199
160 | 14.6 | 125 | 160x14,6 | 6669.1 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -3221 | -328.3384 | 6.728 | 13.43
200 | 18.2 | 150 | 200x18,2 | 10394.8 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -5021 | -511.8247 | 10.48 | 21.01
250 | 22.7 | 200 | 250x22,7 | 16209.7 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -7829 | -798.0632 | 16.3 | 32.861
315 | 28.6 | 250 | 315x28,6 | 25733 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -12429 | -1266.9725 | 25.68 | 52.172
355 | 32.2 | 300 | 355x32,2 | 32654.3 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -15772 | -1607.7472 | 32.6 | 66.29
400 | 36.3 | 300 | 400x36,3 | 41476.4 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -20033 | -2042.0999 | 41.407 | 84.29
450 | 40.9 | 400 | 450x40,9 | 52565.8 | 5 | 20 | 40 | 20 | -11.5 | 1200 | 0.035 | -25389 | -2588.0734 | 52.478 | 106.477
Linear expansion forces Climatherm Faser SDR17.6
Pipe diameter [mm] | Wall thickness [mm] | [DN] | Bore [mm] | Area [mm²] | Ambient Temp during processing [° C] | Ambient Temp during operation [° C] | Medium Temp during processing [° C] | Medium Temp during operation [° C] | ΔT [°C] | E modulus [N/mm²] | α (Uitzettingscoeff.) [mm/°C*m] | F (Reaktion Force) [N] | F (Reaktion Force) [kgf] | Weight pipe | Weight water content
|  |  |  | afronden((3,14/4)*(A5^2-(A5-2*B5)^2);1 |  |  |  |  | 0.1*(G5-F5)+0.65*(I5-H5) |  |  | afronden((E5*J5*K5*(L5/1000));1 | M5/9,81 | kg / m | kg / m
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
160 | 9.1 | 150 | 160x9,1 | 4314 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 1187 | 120.999 | 4.36 | 15.792
200 | 11.4 | 200 | 200x11,4 | 6754.6 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 1858 | 189.3986 | 6.798 | 24.661
250 | 14.2 | 250 | 250x14,2 | 10519.2 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 2894 | 295.0051 | 10.574 | 38.568
315 | 17.9 | 300 | 315x17,9 | 16707.3 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 4596 | 468.5015 | 16.735 | 61.223
355 | 20.1 | 350 | 355x20,1 | 21147.6 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 5818 | 593.0683 | 21.206 | 77.832
400 | 22.7 | 350 | 400x22,7 | 26906.9 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 7402 | 754.5362 | 26.93 | 98.756
450 | 25.5 | 400 | 450x25,5 | 34007 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 9355 | 953.6188 | 34.021 | 125.036
500 | 28.4 | 450 | 500x28,4 | 42076.8 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 11575 | 1179.9185 | 42.072 | 154.272
560 | 31.7 | 500 | 560x31,7 | 52612.7 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 14474 | 1475.4332 | 52.554 | 193.688
630 | 35.7 | 500 | 630x35,7 | 66653.8 | 10 | 30 | 5 | 12 | 6.55 | 1200 | 0.035 | 18336 | 1869.1131 | 66.542 | 245.07
Note on K2: Laan, Dennis: Is E modulus Faser buis bij 20C
Note on L2: Laan, Dennis: Linear expansion of Faser pipes
Note on K22: Laan, Dennis: Is E modulusFaser bij 20C
Note on L22: Laan, Dennis: Linear expansion Faser pipes
Note on K44: Laan, Dennis: Is E modulusFaser bij 20C
Note on L44: Laan, Dennis: Linear expansion Faser pipes