## Working Pressure Comparison
Comparison of pressure ratings (service life of 25 years), Copper AS 1432, Type A & B vs. aquatherm green pipe SDR9 MF RP
1) Potable water temperature 20°C
|  |  | Copper (AS 1432 Type A) 20°C |  |  |  | aquatherm green pipe SDR9 MF RP 20°C
| Stress | Nominal Bore | OD | Thickness | Safe Working Pressure | OD | Wall thickness | di | Permissible Working Pressure
| Mpa | mm | max, mm | mm | kPa | mm | mm | mm | kPa
| 41 | 18 | 15.88 | 1.04 | 5750
|  | 20 | 19.05 | 1.21 | 5560 | 20 | 2.8 | 14.4 | 2530
|  | 25 | 25.4 | 1.39 | 4750 | 25 | 3.5 | 18 | 2530
|  | 32 | 31.75 | 1.39 | 3750 | 32 | 3.6 | 24.8 | 2350
|  | 40 | 38.1 | 1.39 | 3100 | 40 | 4.5 | 31 | 2350
|  | 50 | 50.8 | 1.39 | 2310 | 50 | 5.6 | 38.8 | 2350
|  | 65 | 63.5 | 1.39 | 1840 | 63 | 7.1 | 48.8 | 2350
|  | 80 | 76.2 | 1.73 | 1900 | 75 | 8.4 | 58.2 | 2350
|  | 90 | 88.9 | 1.73 | 1630 | 90 | 10.1 | 69.8 | 2350
|  | 100 | 101.6 | 1.83 | 1500 | 110 | 12.3 | 85.4 | 2350
|  | 125 | 127 | 1.83 | 1200 | 125 | 14 | 97 | 2350
|  | 150 | 152.4 | 2.38 | 1300 | 160 | 17.9 | 124.2 | 2350
|  | 200 | 203.2 | 2.24 | 910 | 200 | 22.4 | 155.2 | 2350
|  |  | Copper (AS 1432 Type B) 20°C |  |  |  | aquatherm green pipe SDR9 MF RP 20°C
| Stress | Nominal Bore | OD | Thickness | Safe Working Pressure | OD | Wall thickness | di | Permissible Working Pressure
| Mpa | mm | max, mm | mm | kPa | mm | mm | mm | kPa
| 41 | 18 | 15.88 | 0.88 | 4810
|  | 20 | 19.05 | 0.88 | 3970 | 20 | 2.8 | 14.4 | 2530
|  | 25 | 25.4 | 1.04 | 3500 | 25 | 3.5 | 18 | 2530
|  | 32 | 31.75 | 1.04 | 2780 | 32 | 3.6 | 24.8 | 2350
|  | 40 | 38.1 | 1.04 | 2300 | 40 | 4.5 | 31 | 2350
|  | 50 | 50.8 | 1.04 | 1710 | 50 | 5.6 | 38.8 | 2350
|  | 65 | 63.5 | 1.04 | 1370 | 63 | 7.1 | 48.8 | 2350
|  | 80 | 76.2 | 1.39 | 1520 | 75 | 8.4 | 58.2 | 2350
|  | 90 | 88.9 | 1.39 | 1300 | 90 | 10.1 | 69.8 | 2350
|  | 100 | 101.6 | 1.47 | 1200 | 110 | 12.3 | 85.4 | 2350
|  | 125 | 127 | 1.47 | 960 | 125 | 14 | 97 | 2350
|  | 150 | 152.4 | 1.83 | 1000 | 160 | 17.9 | 124.2 | 2350
|  | 200 | 200 | 1.78 | 720 | 200 | 22.4 | 155.2 | 2350
2) Potable water temperature 50°C
|  |  | Copper (AS 1432 Type A) 50°C |  |  |  | aquatherm green pipe SDR9 MF RP 50°C
| Stress | Nominal Bore | OD | Thickness | Safe Working Pressure | OD | Wall thickness | di | Permissible Working Pressure
| Mpa | mm | max, mm | mm | kPa | mm | mm | mm | kPa
| 41 | 18 | 15.88 | 1.04 | 5750
|  | 20 | 19.05 | 1.21 | 5560 | 20 | 2.8 | 14.4 | 1520
|  | 25 | 25.4 | 1.39 | 4750 | 25 | 3.5 | 18 | 1520
|  | 32 | 31.75 | 1.39 | 3750 | 32 | 3.6 | 24.8 | 1480
|  | 40 | 38.1 | 1.39 | 3100 | 40 | 4.5 | 31 | 1480
|  | 50 | 50.8 | 1.39 | 2310 | 50 | 5.6 | 38.8 | 1480
|  | 65 | 63.5 | 1.39 | 1840 | 63 | 7.1 | 48.8 | 1480
|  | 80 | 76.2 | 1.73 | 1900 | 75 | 8.4 | 58.2 | 1480
|  | 90 | 88.9 | 1.73 | 1630 | 90 | 10.1 | 69.8 | 1480
|  | 100 | 101.6 | 1.83 | 1500 | 110 | 12.3 | 85.4 | 1480
|  | 125 | 127 | 1.83 | 1200 | 125 | 14 | 97 | 1480
|  | 150 | 152.4 | 2.38 | 1300 | 160 | 17.9 | 124.2 | 1480
|  | 200 | 203.2 | 2.24 | 910 | 200 | 22.4 | 155.2 | 1480
|  |  | Copper (AS 1432 Type B) 50°C |  |  |  | aquatherm green pipe SDR9 MF RP 50°C
| Stress | Nominal Bore | OD | Thickness | Safe Working Pressure | OD | Wall thickness | di | Permissible Working Pressure
| Mpa | mm | max, mm | mm | kPa | mm | mm | mm | kPa
| 41 | 18 | 15.88 | 0.88 | 4810
|  | 20 | 19.05 | 0.88 | 3970 | 20 | 2.8 | 14.4 | 1520
|  | 25 | 25.4 | 1.04 | 3500 | 25 | 3.5 | 18 | 1520
|  | 32 | 31.75 | 1.04 | 2780 | 32 | 3.6 | 24.8 | 1480
|  | 40 | 38.1 | 1.04 | 2300 | 40 | 4.5 | 31 | 1480
|  | 50 | 50.8 | 1.04 | 1710 | 50 | 5.6 | 38.8 | 1480
|  | 65 | 63.5 | 1.04 | 1370 | 63 | 7.1 | 48.8 | 1480
|  | 80 | 76.2 | 1.39 | 1520 | 75 | 8.4 | 58.2 | 1480
|  | 90 | 88.9 | 1.39 | 1300 | 90 | 10.1 | 69.8 | 1480
|  | 100 | 101.6 | 1.47 | 1200 | 110 | 12.3 | 85.4 | 1480
|  | 125 | 127 | 1.47 | 960 | 125 | 14 | 97 | 1480
|  | 150 | 152.4 | 1.83 | 1000 | 160 | 17.9 | 124.2 | 1480
|  | 200 | 200 | 1.78 | 720 | 200 | 22.4 | 155.2 | 1480
3) Potable water temperature 65°C (= Flow temperature Hot Potable Water Reticulation Systems)
|  |  | Copper (AS 1432 Type A) 65°C (T= 0.83) |  |  |  | aquatherm green pipe SDR9 MF RP 65°C
| Stress | Nominal Bore | OD | Thickness | Safe Working Pressure | OD | Wall thickness | di | Permissible Working Pressure
| Mpa | mm | max, mm | mm | kPa | mm | mm | mm | kPa
| 41 | 18 | 15.88 | 1.04 | 4772.5
|  | 20 | 19.05 | 1.21 | 4614.8 | 20 | 2.8 | 14.4 | 1200
|  | 25 | 25.4 | 1.39 | 3942.5 | 25 | 3.5 | 18 | 1200
|  | 32 | 31.75 | 1.39 | 3112.5 | 32 | 3.6 | 24.8 | 1140
|  | 40 | 38.1 | 1.39 | 2573 | 40 | 4.5 | 31 | 1140
|  | 50 | 50.8 | 1.39 | 1917.3 | 50 | 5.6 | 38.8 | 1140
|  | 65 | 63.5 | 1.39 | 1527.2 | 63 | 7.1 | 48.8 | 1140
|  | 80 | 76.2 | 1.73 | 1577 | 75 | 8.4 | 58.2 | 1140
|  | 90 | 88.9 | 1.73 | 1352.9 | 90 | 10.1 | 69.8 | 1140
|  | 100 | 101.6 | 1.83 | 1245 | 110 | 12.3 | 85.4 | 1140
|  | 125 | 127 | 1.83 | 996 | 125 | 14 | 97 | 1140
|  | 150 | 152.4 | 2.38 | 1079 | 160 | 17.9 | 124.2 | 1140
|  | 200 | 203.2 | 2.24 | 755.3 | 200 | 22.4 | 155.2 | 1140
|  |  | Copper (AS 1432 Type B) 65°C (T= 0.83) |  |  |  | aquatherm green pipe SDR9 MF RP 65°C
| Stress | Nominal Bore | OD | Thickness | Safe Working Pressure | OD | Wall thickness | di | Permissible Working Pressure
| Mpa | mm | max, mm | mm | kPa | mm | mm | mm | kPa
| 41 | 18 | 15.88 | 0.88 | 3992.3
|  | 20 | 19.05 | 0.88 | 3295.1 | 20 | 2.8 | 14.4 | 1200
|  | 25 | 25.4 | 1.04 | 2905 | 25 | 3.5 | 18 | 1200
|  | 32 | 31.75 | 1.04 | 2307.4 | 32 | 3.6 | 24.8 | 1140
|  | 40 | 38.1 | 1.04 | 1909 | 40 | 4.5 | 31 | 1140
|  | 50 | 50.8 | 1.04 | 1419.3 | 50 | 5.6 | 38.8 | 1140
|  | 65 | 63.5 | 1.04 | 1137.1 | 63 | 7.1 | 48.8 | 1140
|  | 80 | 76.2 | 1.39 | 1261.6 | 75 | 8.4 | 58.2 | 1140
|  | 90 | 88.9 | 1.39 | 1079 | 90 | 10.1 | 69.8 | 1140
|  | 100 | 101.6 | 1.47 | 996 | 110 | 12.3 | 85.4 | 1140 | `
|  | 125 | 127 | 1.47 | 796.8 | 125 | 14 | 97 | 1140
|  | 150 | 152.4 | 1.83 | 830 | 160 | 17.9 | 124.2 | 1140
|  | 200 | 200 | 1.78 | 597.6 | 200 | 22.4 | 155.2 | 1140
Note on H16: SDR7.4 MF
Note on H17: SDR7.4 MF
Note on H34: SDR7.4 MF
Note on H35: SDR7.4 MF
Note on H53: SDR7.4 MF
Note on H54: SDR7.4 MF
Note on H71: SDR7.4 MF
Note on H72: SDR7.4 MF
Note on H90: SDR7.4 MF
Note on H91: SDR7.4 MF
Note on H108: SDR7.4 MF
Note on H109: SDR7.4 MF