## aquatherm green pipe SDR11 S
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
m³/h | l/h | l/min | l/s
4 | 4000 | 66.6667 | 1.1111 | aquatherm green pipe SDR11 S vs Copper AS 1432 : 2000 type B pipe
1 | 1000 | 16.6667 | 0.27778 | (cold drinking water application)
72 | 72000 | 1200 | 20 | (velocity [m/s] => flow rate [l/s or l/h])
720 | 720000 | 12000 | 200 |  |  |  |  | Only the green cells can be edited
| Copper pipe |  |  | aquatherm green pipe |  |  |  | Copper pipe | aquatherm green pipe | Copper pipe | aquatherm green pipe
Flange | AS 1432 : 2000 type B |  |  | SDR11 |  |  | velocity | AS 1432 : 2000 type B | SDR11 | AS 1432 : 2000 type B | SDR11
DN | OD | wall | bore | ø | wall | bore | m/s | l/s | l/s | l/h | l/h
15 | 19.1 | 1 | 17.1 | 20 | 1.9 | 16.2 | 2 | 0.4593 | 0.41223 | 1653.4908 | 1484.0195
20 | 25.4 | 1.2 | 23 | 25 | 2.3 | 20.4 | 1.5 | 0.6232 | 0.49026 | 2243.5022 | 1764.945
25 | 31.8 | 1.2 | 29.4 | 32 | 2.9 | 26.2 | 1 | 0.67885 | 0.53911 | 2443.8482 | 1940.8061
32 | 38.1 | 1.2 | 35.7 | 40 | 3.7 | 32.6 | 1.4 | 1.4013 | 1.1685 | 5044.801 | 4206.7123
40 | 50.8 | 1.2 | 48.4 | 50 | 4.6 | 40.8 | 0.07 | 0.12879 | 0.091516 | 463.6266 | 329.4564
50 | 63.5 | 1.2 | 61.1 | 63 | 5.8 | 51.4 | 1 | 2.932 | 2.0749 | 10555.0913 | 7469.7456
65 | 76.2 | 1.6 | 73 | 75 | 6.8 | 61.4 | 1.7 | 7.1149 | 5.0334 | 25613.8119 | 18120.2939
80 | 88.9 | 1.6 | 85.7 | 90 | 8.2 | 73.6 | 3 | 17.3045 | 12.763 | 62296.3314 | 45946.9256
100 | 101.6 | 1.6 | 98.4 | 110 | 10 | 90 | 2 | 15.2089 | 12.7231 | 54751.972 | 45803.07
125 | 127 | 1.6 | 123.8 | 125 | 11.4 | 102.2 | 1.5 | 18.0555 | 12.3047 | 64999.8152 | 44296.8276
150 | 152.4 | 2 | 148.4 | 160 | 14.6 | 130.8 | 2 | 34.5919 | 26.8734 | 124530.97 | 96744.2266
200 | 203.2 | 2 | 199.2 | 200 | 18.2 | 163.6 | 2 | 62.3284 | 42.0411 | 224382.115 | 151347.8193
m³/h | l/h | l/min | l/s
0.72 | 720 | 12 | 0.2 | aquatherm green pipe SDR11 S vs Copper AS 1432 : 2000 type B pipe
0.72 | 720 | 12 | 0.2 | (cold drinking water application)
0.72 | 720 | 12 | 0.2 | (flow rate [l/s] => velocity [m/s])
0.72 | 720 | 12 | 0.2 |  |  |  | Only the green cells can be edited
| Copper pipe |  |  | aquatherm green pipe |  |  | Copper pipe | aquatherm green pipe | Copper pipe | aquatherm green pipe
Flange | AS 1432 : 2000 type B |  |  | SDR11 |  |  | AS 1432 : 2000 type B | SDR11 | AS 1432 : 2000 type B | SDR11
DN | OD | wall | bore | ø | wall | bore | l/s | l/s | m/s | m/s
15 | 19.1 | 1 | 17.1 | 20 | 1.9 | 16.2 | 1.1 | 0.34 | 4.7899 | 1.6496
20 | 25.4 | 1.2 | 23 | 25 | 2.3 | 20.4 | 1.1 | 0.34 | 2.6476 | 1.0403
25 | 31.8 | 1.2 | 29.4 | 32 | 2.9 | 26.2 | 1 | 0.34 | 1.4731 | 0.63067
32 | 38.1 | 1.2 | 35.7 | 40 | 3.7 | 32.6 | 1.5 | 0.34 | 1.4986 | 0.40735
40 | 50.8 | 1.2 | 48.4 | 50 | 4.6 | 40.8 | 0.34 | 0.34 | 0.1848 | 0.26006
50 | 63.5 | 1.2 | 61.1 | 63 | 5.8 | 51.4 | 0.34 | 0.34 | 0.11596 | 0.16386
65 | 76.2 | 1.6 | 73 | 75 | 6.8 | 61.4 | 0.34 | 0.34 | 0.081237 | 0.11483
80 | 88.9 | 1.6 | 85.7 | 90 | 8.2 | 73.6 | 0.34 | 0.34 | 0.058944 | 0.079918
100 | 101.6 | 1.6 | 98.4 | 110 | 10 | 90 | 0.34 | 0.34 | 0.044711 | 0.053446
125 | 127 | 1.6 | 123.8 | 125 | 11.4 | 102.2 | 0.34 | 0.34 | 0.028246 | 0.041448
150 | 152.4 | 2 | 148.4 | 160 | 14.6 | 130.8 | 0.34 | 0.34 | 0.019658 | 0.025304
200 | 203.2 | 2 | 199.2 | 200 | 18.2 | 163.6 | 0.34 | 0.34 | 0.01091 | 0.016175
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on I15: Recommended velocities: < 2.0 m/s (cold water riser pipes) < 1.5 m/s (cold water pipes)
Note on K40: Recommended velocities: < 2.0 m/s (cold water riser pipes) < 1.5 m/s (cold water pipes)
Note on L40: Recommended velocities: < 2.0 m/s (cold water riser pipes) < 1.5 m/s (cold water pipes)

## aquatherm green pipe SDR7,4 MF
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
m³/h | l/h | l/min | l/s
5 | 5000 | 83.3333 | 1.3889 | aquatherm green pipe SDR7,4 MF vs Copper AS 1432 : 2000 type B pipe
10 | 10000 | 166.6667 | 2.7778 | (cold & hot (recirculating) drinking water applications)
0.9 | 900 | 15 | 0.25 | (velocity [m/s] => flow rate [l/s or l/h])
10.8 | 10800 | 180 | 3 |  |  |  |  | Only the green cells can be edited
| Copper pipe |  |  | aquatherm green pipe MF |  |  |  | Copper pipe | aquatherm green pipe MF | Copper pipe | aquatherm green pipe MF
Flange | AS 1432 : 2000 type B |  |  | SDR7.4 |  |  | velocity | AS 1432 : 2000 type B | SDR7.4 | AS 1432 : 2000 type B | SDR7.4
DN | OD | wall | bore | ø | wall | bore | m/s | l/s | l/s | l/h | l/h
15 | 19.1 | 1 | 17.1 | 20 | 2.8 | 14.4 | 1 | 0.22965 | 0.16286 | 826.7454 | 586.2793
20 | 25.4 | 1.2 | 23 | 25 | 3.5 | 18 | 1 | 0.41546 | 0.25446 | 1495.6682 | 916.0614
25 | 31.8 | 1.2 | 29.4 | 32 | 4.4 | 23.2 | 1 | 0.67885 | 0.42272 | 2443.8482 | 1521.7929
32 | 38.1 | 1.2 | 35.7 | 40 | 5.5 | 29 | 1 | 1.001 | 0.6605 | 3603.4293 | 2377.8014
40 | 50.8 | 1.2 | 48.4 | 50 | 6.9 | 36.2 | 1 | 1.8398 | 1.0292 | 6623.237 | 3705.0725
50 | 63.5 | 1.2 | 61.1 | 63 | 8.6 | 45.8 | 1.6 | 4.6912 | 2.6359 | 16888.1461 | 9489.2199
65 | 76.2 | 1.6 | 73 | 75 | 10.3 | 54.4 | 2 | 8.3705 | 4.6484 | 30133.8963 | 16734.293
80 | 88.9 | 1.6 | 85.7 | 90 | 12.3 | 65.4 | 1.4 | 8.0755 | 4.7028 | 29071.6213 | 16930.2397
100 | 101.6 | 1.6 | 98.4 | 110 | 15.1 | 79.8 | 1 | 7.6044 | 5.0013 | 27375.986 | 18004.6779
125 | 127 | 1.6 | 123.8 | 125 | 17.1 | 90.8 | 1 | 12.037 | 6.4751 | 43333.2101 | 23310.4829
150 | 152.4 | 2 | 148.4 | 160 | 21.9 | 116.2 | 1 | 17.296 | 10.6045 | 62265.485 | 38176.1237
200 | 203.2 | 2 | 199.2 | 200 | 27.4 | 145.2 | 1 | 31.1642 | 16.5581 | 112191.0575 | 59609.1331
m³/h | l/h | l/min | l/s
0.72 | 720 | 12 | 0.2 | aquatherm green pipe SDR7,4 MF vs Copper AS 1432 : 2000 type B pipe
0.72 | 720 | 12 | 0.2 | (cold & hot (recirculating) drinking water applications)
0.9 | 900 | 15 | 0.25 | (flow rate [l/s] => velocity [m/s])
6.66 | 6660 | 111 | 1.85 |  |  |  | Only the green cells can be edited
| Copper pipe |  |  | aquatherm green pipe MF |  |  | Copper pipe | aquatherm green pipe MF | Copper pipe | aquatherm green pipe MF
Flange | AS 1432 : 2000 type B |  |  | SDR7.4 |  |  | AS 1432 : 2000 type B | SDR7.4 | AS 1432 : 2000 type B | SDR7.4
DN | OD | wall | bore | ø | wall | bore | l/s | l/s | m/s | m/s
15 | 19.1 | 1 | 17.1 | 20 | 2.8 | 14.4 | 1.1 | 0.2 | 4.7899 | 1.2281
20 | 25.4 | 1.2 | 23 | 25 | 3.5 | 18 | 1.1 | 0.6 | 2.6476 | 2.3579
25 | 31.8 | 1.2 | 29.4 | 32 | 4.4 | 23.2 | 0.34 | 0.34 | 0.50085 | 0.80431
32 | 38.1 | 1.2 | 35.7 | 40 | 5.5 | 29 | 0.9 | 0.34 | 0.89914 | 0.51476
40 | 50.8 | 1.2 | 48.4 | 50 | 6.9 | 36.2 | 0.34 | 0.9 | 0.1848 | 0.87448
50 | 63.5 | 1.2 | 61.1 | 63 | 8.6 | 45.8 | 0.34 | 0.34 | 0.11596 | 0.20638
65 | 76.2 | 1.6 | 73 | 75 | 10.3 | 54.4 | 0.34 | 0.34 | 0.081237 | 0.14629
80 | 88.9 | 1.6 | 85.7 | 90 | 12.3 | 65.4 | 0.34 | 0.34 | 0.058944 | 0.10122
100 | 101.6 | 1.6 | 98.4 | 110 | 15.1 | 79.8 | 0.34 | 0.34 | 0.044711 | 0.067982
125 | 127 | 1.6 | 123.8 | 125 | 17.1 | 90.8 | 0.34 | 0.34 | 0.028246 | 0.052509
150 | 152.4 | 2 | 148.4 | 160 | 21.9 | 116.2 | 0.34 | 0.34 | 0.019658 | 0.032062
200 | 203.2 | 2 | 199.2 | 200 | 27.4 | 145.2 | 0.34 | 0.34 | 0.01091 | 0.020534
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on I15: Recommended velocities: max. 2.0 m/s (cold & hot water complete aquatherm green pipe system) < 1.5 m/s (mixed (Cu/PP-R) water ≤ 60⁰C) max. 0.9 m/s (mixed (Cu/PP-R) hot water recirculation pipes > 60⁰C)
Note on K40: Recommended velocities: < 2.0 m/s (cold water riser pipes) < 1.5 m/s (cold water pipes & hot water ≤ 60⁰C) max. 0.9 m/s (hot water > 60⁰C & hot water recirculation pipes)
Note on L40: Recommended velocities: max. 2.0 m/s (cold & hot water complete aquatherm green pipe system) < 1.5 m/s (mixed (Cu/PP-R) water ≤ 60⁰C) max. 0.9 m/s (mixed (Cu/PP-R) hot water recirculation pipes > 60⁰C)

## Dimensions
| aquatherm green pipe SDR11 S |  |  |  | Copper tube AS 1432 : 2000 type B
Flange | OD | Wall thickness | Dimensions | Bore | OD | Wall thickness | Dimensions | Bore
[DN] | mm | mm | mm | mm | mm | mm | mm | mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
15 | 20 | 1.9 | 20x1,9 | 16.2 | 19.1 | 1 | 19.1x1.0 | 17.1
20 | 25 | 2.3 | 25x2,3 | 20.4 | 25.4 | 1.2 | 25.4x1.2 | 23
25 | 32 | 2.9 | 32x2,9 | 26.2 | 31.8 | 1.2 | 31.8x1.2 | 29.4
32 | 40 | 3.7 | 40x3,7 | 32.6 | 38.1 | 1.2 | 38.1x1.2 | 35.7
40 | 50 | 4.6 | 50x4,6 | 40.8 | 50.8 | 1.2 | 50.8x1.2 | 48.4
50 | 63 | 5.8 | 63x5,8 | 51.4 | 63.5 | 1.2 | 63.5x1.2 | 61.1
65 | 75 | 6.8 | 75x6,8 | 61.4 | 76.2 | 1.6 | 76.2x1.6 | 73
80 | 90 | 8.2 | 90x8,2 | 73.6 | 88.9 | 1.6 | 88.9x1.6 | 85.7
100 | 110 | 10 | 110x10,0 | 90 | 101.6 | 1.6 | 101.6x1.6 | 98.4
125 | 125 | 11.4 | 125x11,4 | 102.2 | 127 | 1.6 | 127.0x1.6 | 123.8
150 | 160 | 14.6 | 160x14,6 | 130.8 | 152.4 | 2 | 152.4x2.0 | 148.4
200 | 200 | 18.2 | 200x18,2 | 163.6 | 203.2 | 2 | 203.2x2.0 | 199.2
| aquatherm green pipe SDR7,4 MF |  |  |  | Copper tube AS 1432 : 2000 type B
Flange | OD | Wall thickness | Dimensions | Bore | OD | Wall thickness | Dimensions | Bore
[DN] | mm | mm | mm | mm | mm | mm | mm | mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
15 | 20 | 2.8 | 20x2,8 | 14.4 | 19.1 | 1 | 19.1x1.0 | 17.1
20 | 25 | 3.5 | 25x3,5 | 18 | 25.4 | 1.2 | 25.4x1.2 | 23
25 | 32 | 4.4 | 32x4,4 | 23.2 | 31.8 | 1.2 | 31.8x1.2 | 29.4
32 | 40 | 5.5 | 40x5,5 | 29 | 38.1 | 1.2 | 38.1x1.2 | 35.7
40 | 50 | 6.9 | 50x6,9 | 36.2 | 50.8 | 1.2 | 50.8x1.2 | 48.4
50 | 63 | 8.6 | 63x8,6 | 45.8 | 63.5 | 1.2 | 63.5x1.2 | 61.1
65 | 75 | 10.3 | 75x10,3 | 54.4 | 76.2 | 1.6 | 76.2x1.6 | 73
80 | 90 | 12.3 | 90x12,3 | 65.4 | 88.9 | 1.6 | 88.9x1.6 | 85.7
100 | 110 | 15.1 | 110x15,1 | 79.8 | 101.6 | 1.6 | 101.6x1.6 | 98.4
125 | 125 | 17.1 | 125x17,1 | 90.8 | 127 | 1.6 | 127.0x1.6 | 123.8
150 | 160 | 21.9 | 160x21,9 | 116.2 | 152.4 | 2 | 152.4x2.0 | 148.4
200 | 200 | 27.4 | 200x27,4 | 145.2 | 203.2 | 2 | 203.2x2.0 | 199.2
Note on F1: Source: Crane copper tube www.cranecopper.com.au
Note on F18: Source: Crane copper tube www.cranecopper.com.au